## Sheet1
PROPERTIES
General
Name | Nordex N133/4.X Mode 1 78, 83m 4,7MW
Manufacturer | Nordex
Hub Height | 78 | 83
Power
Rated Power | 4700
Peak Power | 4700
Power Regulation Type | Pitch
Voltage | 690
Rotor
Rotor diameter | 133
Number of blades | 3
Rated RPM | 11.4
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 28
Restart Wind Speed | 22
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 40
High Temperature Restart | 38
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | S
Values
Certification | IEC 3rd Edition
Vave | 9
Vref | 47
Design TI | 0.11

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 12 | 14 | 15 | 17 | 19 | 21 | 23 | 24 | 26 | 28 | 30 | 31 | 33
| 3.5 | 67 | 70 | 74 | 77 | 80 | 83 | 86 | 89 | 92 | 96 | 99 | 102 | 105
| 4 | 144 | 149 | 154 | 159 | 164 | 169 | 174 | 179 | 184 | 189 | 194 | 200 | 205
| 4.5 | 239 | 247 | 254 | 262 | 269 | 277 | 284 | 291 | 299 | 306 | 314 | 321 | 329
| 5 | 355 | 365 | 375 | 385 | 396 | 406 | 416 | 427 | 437 | 447 | 458 | 468 | 478
| 5.5 | 492 | 506 | 520 | 534 | 547 | 561 | 575 | 589 | 602 | 616 | 630 | 643 | 657
| 6 | 656 | 674 | 692 | 710 | 728 | 745 | 763 | 781 | 799 | 817 | 835 | 852 | 870
| 6.5 | 850 | 872 | 895 | 918 | 940 | 963 | 985 | 1008 | 1031 | 1053 | 1076 | 1098 | 1121
| 7 | 1075 | 1103 | 1131 | 1160 | 1188 | 1216 | 1244 | 1272 | 1300 | 1329 | 1357 | 1385 | 1413
| 7.5 | 1334 | 1369 | 1403 | 1438 | 1473 | 1507 | 1542 | 1576 | 1611 | 1645 | 1680 | 1714 | 1749
| 8 | 1629 | 1671 | 1713 | 1755 | 1797 | 1839 | 1881 | 1922 | 1964 | 2006 | 2048 | 2090 | 2131
| 8.5 | 1959 | 2009 | 2059 | 2109 | 2159 | 2209 | 2259 | 2308 | 2357 | 2405 | 2452 | 2498 | 2543
| 9 | 2307 | 2366 | 2424 | 2483 | 2541 | 2599 | 2658 | 2716 | 2770 | 2820 | 2868 | 2914 | 2958
| 9.5 | 2655 | 2722 | 2789 | 2856 | 2923 | 2990 | 3057 | 3124 | 3179 | 3230 | 3277 | 3321 | 3363
| 10 | 2991 | 3067 | 3142 | 3217 | 3292 | 3367 | 3442 | 3520 | 3576 | 3625 | 3669 | 3709 | 3746
| 10.5 | 3308 | 3391 | 3474 | 3557 | 3640 | 3724 | 3803 | 3883 | 3935 | 3979 | 4014 | 4044 | 4071
| 11 | 3601 | 3691 | 3782 | 3872 | 3953 | 4034 | 4104 | 4170 | 4210 | 4244 | 4269 | 4290 | 4309
| 11.5 | 3873 | 3967 | 4052 | 4135 | 4202 | 4269 | 4326 | 4380 | 4410 | 4435 | 4453 | 4468 | 4481
| 12 | 4111 | 4194 | 4265 | 4333 | 4388 | 4442 | 4486 | 4528 | 4549 | 4567 | 4579 | 4588 | 4597
| 12.5 | 4299 | 4368 | 4425 | 4481 | 4522 | 4563 | 4595 | 4625 | 4639 | 4651 | 4658 | 4662 | 4666
| 13 | 4443 | 4498 | 4542 | 4585 | 4614 | 4643 | 4663 | 4679 | 4687 | 4693 | 4696 | 4697 | 4697
| 13.5 | 4549 | 4592 | 4623 | 4653 | 4670 | 4687 | 4695 | 4698 | 4700 | 4700 | 4700 | 4700 | 4700
| 14 | 4625 | 4654 | 4673 | 4691 | 4695 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 14.5 | 4673 | 4690 | 4696 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 15 | 4695 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 15.5 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 16 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 16.5 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 17 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 17.5 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 18 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 18.5 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 19 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 19.5 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 20 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 20.5 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 21 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 21.5 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 22 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 22.5 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 23 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 23.5 | 4694 | 4694 | 4694 | 4694 | 4694 | 4694 | 4694 | 4694 | 4694 | 4694 | 4694 | 4694 | 4694
| 24 | 4673 | 4673 | 4673 | 4673 | 4673 | 4673 | 4673 | 4673 | 4673 | 4673 | 4673 | 4673 | 4673
| 24.5 | 4637 | 4637 | 4637 | 4637 | 4637 | 4637 | 4637 | 4637 | 4637 | 4637 | 4637 | 4637 | 4637
| 25 | 4594 | 4594 | 4594 | 4594 | 4594 | 4594 | 4594 | 4594 | 4594 | 4594 | 4594 | 4594 | 4594
| 25.5 | 4550 | 4550 | 4550 | 4550 | 4550 | 4550 | 4550 | 4550 | 4550 | 4550 | 4550 | 4550 | 4550
| 26 | 4502 | 4502 | 4502 | 4502 | 4502 | 4502 | 4502 | 4502 | 4502 | 4502 | 4502 | 4502 | 4502
| 26.5 | 4459 | 4459 | 4459 | 4459 | 4459 | 4459 | 4459 | 4459 | 4459 | 4459 | 4459 | 4459 | 4459
| 27 | 4411 | 4411 | 4411 | 4411 | 4411 | 4411 | 4411 | 4411 | 4411 | 4411 | 4411 | 4411 | 4411
| 27.5 | 4368 | 4368 | 4368 | 4368 | 4368 | 4368 | 4368 | 4368 | 4368 | 4368 | 4368 | 4368 | 4368
| 28 | 4320 | 4320 | 4320 | 4320 | 4320 | 4320 | 4320 | 4320 | 4320 | 4320 | 4320 | 4320 | 4320

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.59931 | 0.59931 | 0.59931 | 0.59931 | 0.59931 | 0.59931 | 0.59931 | 0.59931 | 0.59931 | 0.59931 | 0.59931 | 0.59931 | 0.59931
| 3.5 | 0.59236 | 0.59236 | 0.59236 | 0.59236 | 0.59236 | 0.59236 | 0.59236 | 0.59236 | 0.59236 | 0.59236 | 0.59236 | 0.59236 | 0.59236
| 4 | 0.58264 | 0.58264 | 0.58264 | 0.58264 | 0.58264 | 0.58264 | 0.58264 | 0.58264 | 0.58264 | 0.58264 | 0.58264 | 0.58264 | 0.58264
| 4.5 | 0.57569 | 0.57569 | 0.57569 | 0.57569 | 0.57569 | 0.57569 | 0.57569 | 0.57569 | 0.57569 | 0.57569 | 0.57569 | 0.57569 | 0.57569
| 5 | 0.57014 | 0.57014 | 0.57014 | 0.57014 | 0.57014 | 0.57014 | 0.57014 | 0.57014 | 0.57014 | 0.57014 | 0.57014 | 0.57014 | 0.57014
| 5.5 | 0.56667 | 0.56667 | 0.56667 | 0.56667 | 0.56667 | 0.56667 | 0.56667 | 0.56667 | 0.56667 | 0.56667 | 0.56667 | 0.56667 | 0.56667
| 6 | 0.56389 | 0.56389 | 0.56389 | 0.56389 | 0.56389 | 0.56389 | 0.56389 | 0.56389 | 0.56389 | 0.56389 | 0.56389 | 0.56389 | 0.56389
| 6.5 | 0.56319 | 0.56319 | 0.56319 | 0.56319 | 0.56319 | 0.56319 | 0.56319 | 0.56319 | 0.56319 | 0.56319 | 0.56319 | 0.56319 | 0.56319
| 7 | 0.5625 | 0.5625 | 0.5625 | 0.5625 | 0.5625 | 0.5625 | 0.5625 | 0.5625 | 0.56319 | 0.56319 | 0.56319 | 0.56319 | 0.5625
| 7.5 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56111 | 0.56111 | 0.56042 | 0.55972 | 0.55764
| 8 | 0.55486 | 0.55486 | 0.55486 | 0.55486 | 0.55486 | 0.55486 | 0.55486 | 0.55486 | 0.55278 | 0.55069 | 0.54861 | 0.54583 | 0.54306
| 8.5 | 0.53958 | 0.53958 | 0.53958 | 0.53958 | 0.53958 | 0.53958 | 0.53958 | 0.53958 | 0.53611 | 0.53333 | 0.52986 | 0.52639 | 0.52222
| 9 | 0.51944 | 0.51944 | 0.51944 | 0.51944 | 0.51944 | 0.51944 | 0.51944 | 0.51944 | 0.51528 | 0.51111 | 0.50694 | 0.50278 | 0.49792
| 9.5 | 0.49514 | 0.49514 | 0.49514 | 0.49514 | 0.49514 | 0.49583 | 0.49514 | 0.49514 | 0.49028 | 0.48542 | 0.47986 | 0.475 | 0.46944
| 10 | 0.46944 | 0.46944 | 0.46944 | 0.46944 | 0.46875 | 0.46806 | 0.46667 | 0.46528 | 0.45972 | 0.45417 | 0.44861 | 0.44306 | 0.43681
| 10.5 | 0.44236 | 0.44167 | 0.44097 | 0.44028 | 0.43819 | 0.43681 | 0.43472 | 0.43333 | 0.42708 | 0.42083 | 0.41528 | 0.40903 | 0.40278
| 11 | 0.41319 | 0.41181 | 0.41042 | 0.40903 | 0.40625 | 0.40486 | 0.40208 | 0.4 | 0.39306 | 0.38681 | 0.38125 | 0.375 | 0.36806
| 11.5 | 0.38264 | 0.38125 | 0.37917 | 0.37708 | 0.37431 | 0.37153 | 0.36875 | 0.36597 | 0.35972 | 0.35347 | 0.34722 | 0.34097 | 0.33403
| 12 | 0.35208 | 0.35 | 0.34722 | 0.34514 | 0.34167 | 0.33889 | 0.33611 | 0.33333 | 0.32639 | 0.32014 | 0.31389 | 0.30764 | 0.30139
| 12.5 | 0.32153 | 0.31875 | 0.31597 | 0.31389 | 0.31042 | 0.30764 | 0.30417 | 0.30139 | 0.29444 | 0.28819 | 0.28194 | 0.27639 | 0.27014
| 13 | 0.29236 | 0.28958 | 0.28681 | 0.28403 | 0.28056 | 0.27708 | 0.27361 | 0.27083 | 0.26458 | 0.25903 | 0.25347 | 0.24792 | 0.24306
| 13.5 | 0.26597 | 0.26319 | 0.25972 | 0.25694 | 0.25347 | 0.25 | 0.24653 | 0.24306 | 0.23819 | 0.23264 | 0.22778 | 0.22292 | 0.21806
| 14 | 0.24236 | 0.23889 | 0.23611 | 0.23264 | 0.22917 | 0.22569 | 0.22222 | 0.21875 | 0.21389 | 0.20903 | 0.20486 | 0.20069 | 0.19653
| 14.5 | 0.22083 | 0.21736 | 0.21389 | 0.21111 | 0.20694 | 0.20417 | 0.2 | 0.19722 | 0.19236 | 0.18819 | 0.18403 | 0.18056 | 0.17639
| 15 | 0.20139 | 0.19792 | 0.19444 | 0.19097 | 0.1875 | 0.18403 | 0.18056 | 0.17708 | 0.17292 | 0.16944 | 0.16597 | 0.16181 | 0.15903
| 15.5 | 0.18333 | 0.18056 | 0.17708 | 0.17361 | 0.17014 | 0.16667 | 0.1625 | 0.15903 | 0.15556 | 0.15208 | 0.14861 | 0.14583 | 0.14306
| 16 | 0.16736 | 0.16389 | 0.16111 | 0.15764 | 0.15347 | 0.15069 | 0.14653 | 0.14306 | 0.14028 | 0.13681 | 0.13403 | 0.13125 | 0.12847
| 16.5 | 0.15278 | 0.14931 | 0.14583 | 0.14306 | 0.13958 | 0.13611 | 0.13264 | 0.12986 | 0.12708 | 0.12431 | 0.12153 | 0.11944 | 0.11667
| 17 | 0.13958 | 0.13681 | 0.13264 | 0.12986 | 0.12639 | 0.12361 | 0.12083 | 0.11806 | 0.11528 | 0.11319 | 0.11111 | 0.10903 | 0.10625
| 17.5 | 0.12778 | 0.12431 | 0.12083 | 0.11806 | 0.11528 | 0.1125 | 0.11042 | 0.10764 | 0.10556 | 0.10347 | 0.10139 | 0.099306 | 0.097917
| 18 | 0.11667 | 0.11389 | 0.11111 | 0.10833 | 0.10556 | 0.10347 | 0.10139 | 0.099306 | 0.097222 | 0.095139 | 0.093056 | 0.091667 | 0.089583
| 18.5 | 0.10764 | 0.10486 | 0.10208 | 0.1 | 0.097917 | 0.095833 | 0.09375 | 0.091667 | 0.089583 | 0.088194 | 0.086111 | 0.084722 | 0.083333
| 19 | 0.1 | 0.097222 | 0.095139 | 0.093056 | 0.090972 | 0.088889 | 0.086806 | 0.084722 | 0.083333 | 0.081944 | 0.079861 | 0.078472 | 0.077083
| 19.5 | 0.093056 | 0.090972 | 0.088889 | 0.086806 | 0.084722 | 0.082639 | 0.08125 | 0.079861 | 0.077778 | 0.076389 | 0.075 | 0.073611 | 0.072222
| 20 | 0.0875 | 0.085417 | 0.083333 | 0.08125 | 0.079861 | 0.077778 | 0.076389 | 0.074306 | 0.072917 | 0.071528 | 0.070833 | 0.069444 | 0.098
| 20.5 | 0.082639 | 0.080556 | 0.078472 | 0.077083 | 0.075 | 0.073611 | 0.072222 | 0.070833 | 0.069444 | 0.098 | 0.096 | 0.094 | 0.092
| 21 | 0.077778 | 0.076389 | 0.074306 | 0.072917 | 0.071528 | 0.069444 | 0.098 | 0.096 | 0.095 | 0.093 | 0.091 | 0.089 | 0.088
| 21.5 | 0.074306 | 0.072917 | 0.070833 | 0.069444 | 0.098 | 0.096 | 0.094 | 0.092 | 0.09 | 0.088 | 0.087 | 0.085 | 0.084
| 22 | 0.070833 | 0.069444 | 0.098 | 0.096 | 0.094 | 0.092 | 0.09 | 0.088 | 0.086 | 0.085 | 0.083 | 0.082 | 0.08
| 22.5 | 0.096 | 0.094 | 0.092 | 0.09 | 0.088 | 0.086 | 0.084 | 0.082 | 0.081 | 0.08 | 0.078 | 0.077 | 0.075
| 23 | 0.089 | 0.088 | 0.086 | 0.084 | 0.082 | 0.081 | 0.079 | 0.077 | 0.075 | 0.075 | 0.073 | 0.072 | 0.07
| 23.5 | 0.084 | 0.082 | 0.08 | 0.079 | 0.077 | 0.075 | 0.074 | 0.072 | 0.07 | 0.07 | 0.068 | 0.067 | 0.066
| 24 | 0.078 | 0.077 | 0.075 | 0.074 | 0.072 | 0.071 | 0.069 | 0.067 | 0.066 | 0.065 | 0.064 | 0.063 | 0.061
| 24.5 | 0.073 | 0.072 | 0.07 | 0.069 | 0.068 | 0.066 | 0.065 | 0.063 | 0.062 | 0.061 | 0.06 | 0.059 | 0.058
| 25 | 0.069 | 0.068 | 0.066 | 0.065 | 0.063 | 0.062 | 0.061 | 0.059 | 0.058 | 0.057 | 0.056 | 0.055 | 0.054
| 25.5 | 0.065 | 0.063 | 0.062 | 0.061 | 0.06 | 0.058 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053 | 0.052 | 0.051
| 26 | 0.061 | 0.06 | 0.059 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053 | 0.051 | 0.051 | 0.05 | 0.049 | 0.048
| 26.5 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053 | 0.052 | 0.051 | 0.049 | 0.048 | 0.048 | 0.047 | 0.046 | 0.045
| 27 | 0.054 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.044 | 0.042
| 27.5 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.043 | 0.042 | 0.041 | 0.04
| 28 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.041 | 0.04 | 0.039 | 0.038