## Sheet1
PROPERTIES
General
Name | Nordex N133/4.X Mode 7 110m 4,09MW
Manufacturer | Nordex
Hub Height | 110
Power
Rated Power | 4090
Peak Power | 4090
Power Regulation Type | Pitch
Voltage | 690
Rotor
Rotor diameter | 133
Number of blades | 3
Rated RPM | 11.4
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 28
Restart Wind Speed | 22
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 40
High Temperature Restart | 38
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | S
Values
Certification | IEC 3rd Edition
Vave | 9
Vref | 47
Design TI | 0.11

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 20 | 22 | 24 | 26 | 27 | 29 | 31 | 33 | 34 | 36 | 38 | 40 | 42
| 3.5 | 76 | 80 | 83 | 86 | 89 | 92 | 95 | 99 | 102 | 105 | 108 | 111 | 115
| 4 | 154 | 159 | 164 | 169 | 175 | 180 | 185 | 190 | 195 | 200 | 205 | 210 | 216
| 4.5 | 251 | 258 | 266 | 273 | 281 | 289 | 296 | 304 | 311 | 319 | 326 | 334 | 341
| 5 | 367 | 378 | 388 | 399 | 409 | 420 | 430 | 441 | 451 | 461 | 472 | 482 | 493
| 5.5 | 507 | 521 | 535 | 549 | 563 | 577 | 591 | 604 | 618 | 632 | 646 | 660 | 674
| 6 | 673 | 691 | 709 | 727 | 745 | 763 | 781 | 799 | 817 | 835 | 853 | 871 | 889
| 6.5 | 869 | 891 | 914 | 937 | 960 | 983 | 1006 | 1028 | 1051 | 1074 | 1097 | 1120 | 1142
| 7 | 1096 | 1124 | 1153 | 1181 | 1209 | 1238 | 1266 | 1295 | 1323 | 1351 | 1380 | 1408 | 1436
| 7.5 | 1352 | 1387 | 1421 | 1456 | 1491 | 1526 | 1560 | 1595 | 1630 | 1664 | 1699 | 1733 | 1768
| 8 | 1621 | 1663 | 1704 | 1745 | 1786 | 1828 | 1869 | 1910 | 1951 | 1993 | 2034 | 2075 | 2116
| 8.5 | 1886 | 1934 | 1982 | 2029 | 2077 | 2125 | 2173 | 2220 | 2268 | 2315 | 2363 | 2410 | 2458
| 9 | 2137 | 2191 | 2244 | 2298 | 2352 | 2406 | 2460 | 2513 | 2567 | 2621 | 2674 | 2728 | 2781
| 9.5 | 2367 | 2427 | 2486 | 2546 | 2605 | 2664 | 2724 | 2783 | 2842 | 2901 | 2960 | 3019 | 3078
| 10 | 2578 | 2643 | 2707 | 2772 | 2836 | 2901 | 2965 | 3029 | 3094 | 3158 | 3222 | 3287 | 3351
| 10.5 | 2774 | 2843 | 2913 | 2982 | 3051 | 3120 | 3189 | 3258 | 3327 | 3397 | 3463 | 3527 | 3591
| 11 | 2958 | 3032 | 3106 | 3179 | 3253 | 3326 | 3400 | 3474 | 3542 | 3608 | 3667 | 3719 | 3771
| 11.5 | 3134 | 3212 | 3290 | 3368 | 3446 | 3524 | 3593 | 3662 | 3718 | 3773 | 3821 | 3862 | 3904
| 12 | 3304 | 3386 | 3468 | 3550 | 3623 | 3693 | 3750 | 3807 | 3853 | 3896 | 3934 | 3965 | 3996
| 12.5 | 3471 | 3556 | 3633 | 3706 | 3766 | 3825 | 3871 | 3917 | 3952 | 3985 | 4013 | 4034 | 4055
| 13 | 3628 | 3702 | 3768 | 3829 | 3878 | 3926 | 3961 | 3996 | 4021 | 4045 | 4062 | 4074 | 4086
| 13.5 | 3757 | 3820 | 3874 | 3923 | 3962 | 3999 | 4025 | 4050 | 4065 | 4078 | 4086 | 4088 | 4090
| 14 | 3861 | 3912 | 3956 | 3994 | 4023 | 4049 | 4065 | 4080 | 4086 | 4089 | 4090 | 4090 | 4090
| 14.5 | 3943 | 3983 | 4016 | 4045 | 4063 | 4080 | 4085 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090
| 15 | 4004 | 4034 | 4057 | 4076 | 4084 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090
| 15.5 | 4048 | 4068 | 4081 | 4089 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090
| 16 | 4076 | 4086 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090
| 16.5 | 4089 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090
| 17 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090
| 17.5 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090
| 18 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090
| 18.5 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090
| 19 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090
| 19.5 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090
| 20 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090
| 20.5 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090
| 21 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090
| 21.5 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090
| 22 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090
| 22.5 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090
| 23 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090
| 23.5 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090
| 24 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090
| 24.5 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090
| 25 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090
| 25.5 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090
| 26 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090
| 26.5 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090
| 27 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090
| 27.5 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090
| 28 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090 | 4090

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.59931 | 0.59931 | 0.59931 | 0.59931 | 0.59931 | 0.59931 | 0.59931 | 0.59931 | 0.59931 | 0.59931 | 0.59931 | 0.59931 | 0.59931
| 3.5 | 0.59236 | 0.59236 | 0.59236 | 0.59236 | 0.59236 | 0.59236 | 0.59236 | 0.59236 | 0.59236 | 0.59236 | 0.59236 | 0.59236 | 0.59236
| 4 | 0.58264 | 0.58264 | 0.58264 | 0.58264 | 0.58264 | 0.58264 | 0.58264 | 0.58264 | 0.58264 | 0.58264 | 0.58264 | 0.58264 | 0.58264
| 4.5 | 0.57569 | 0.57569 | 0.57569 | 0.57569 | 0.57569 | 0.57569 | 0.57569 | 0.57569 | 0.57569 | 0.57569 | 0.57569 | 0.57569 | 0.57569
| 5 | 0.57014 | 0.57014 | 0.57014 | 0.57014 | 0.57014 | 0.57014 | 0.57014 | 0.57014 | 0.57014 | 0.57014 | 0.57014 | 0.57014 | 0.57014
| 5.5 | 0.56667 | 0.56667 | 0.56667 | 0.56667 | 0.56667 | 0.56667 | 0.56667 | 0.56667 | 0.56667 | 0.56667 | 0.56667 | 0.56667 | 0.56667
| 6 | 0.56389 | 0.56389 | 0.56389 | 0.56389 | 0.56389 | 0.56389 | 0.56389 | 0.56389 | 0.56389 | 0.56389 | 0.56389 | 0.56389 | 0.56389
| 6.5 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181
| 7 | 0.55347 | 0.55347 | 0.55347 | 0.55347 | 0.55347 | 0.55347 | 0.55347 | 0.55347 | 0.55347 | 0.55347 | 0.55347 | 0.55347 | 0.55347
| 7.5 | 0.53472 | 0.53472 | 0.53472 | 0.53472 | 0.53472 | 0.53472 | 0.53472 | 0.53472 | 0.53472 | 0.53472 | 0.53472 | 0.53472 | 0.53472
| 8 | 0.51042 | 0.51042 | 0.51042 | 0.51042 | 0.51042 | 0.51042 | 0.51042 | 0.51042 | 0.51042 | 0.51042 | 0.51042 | 0.51042 | 0.51042
| 8.5 | 0.48194 | 0.48194 | 0.48194 | 0.48194 | 0.48194 | 0.48194 | 0.48194 | 0.48194 | 0.48194 | 0.48194 | 0.48194 | 0.48194 | 0.48194
| 9 | 0.45069 | 0.45069 | 0.45069 | 0.45069 | 0.45069 | 0.45069 | 0.45069 | 0.45069 | 0.45069 | 0.45069 | 0.45069 | 0.45139 | 0.45139
| 9.5 | 0.41944 | 0.41944 | 0.41944 | 0.41944 | 0.41944 | 0.41944 | 0.41944 | 0.41944 | 0.41944 | 0.41944 | 0.41944 | 0.41944 | 0.41875
| 10 | 0.3875 | 0.3875 | 0.3875 | 0.3875 | 0.3875 | 0.3875 | 0.3875 | 0.3875 | 0.3875 | 0.38681 | 0.38611 | 0.38542 | 0.38403
| 10.5 | 0.35625 | 0.35625 | 0.35625 | 0.35625 | 0.35625 | 0.35625 | 0.35556 | 0.35556 | 0.35417 | 0.35347 | 0.35208 | 0.35069 | 0.34931
| 11 | 0.32569 | 0.32569 | 0.32569 | 0.32569 | 0.325 | 0.325 | 0.32361 | 0.32292 | 0.32083 | 0.31944 | 0.31806 | 0.31597 | 0.31458
| 11.5 | 0.29792 | 0.29792 | 0.29722 | 0.29653 | 0.29514 | 0.29444 | 0.29306 | 0.29167 | 0.28958 | 0.28819 | 0.28611 | 0.28403 | 0.28264
| 12 | 0.27222 | 0.27153 | 0.27083 | 0.26944 | 0.26806 | 0.26667 | 0.26528 | 0.26389 | 0.26181 | 0.25972 | 0.25764 | 0.25556 | 0.25347
| 12.5 | 0.24931 | 0.24792 | 0.24722 | 0.24583 | 0.24375 | 0.24236 | 0.24028 | 0.23889 | 0.23681 | 0.23472 | 0.23264 | 0.22986 | 0.22778
| 13 | 0.22847 | 0.22708 | 0.22569 | 0.22361 | 0.22222 | 0.22014 | 0.21806 | 0.21597 | 0.21389 | 0.21181 | 0.20972 | 0.20694 | 0.20486
| 13.5 | 0.20903 | 0.20764 | 0.20625 | 0.20417 | 0.20208 | 0.20069 | 0.19861 | 0.19653 | 0.19375 | 0.19167 | 0.18958 | 0.18681 | 0.18472
| 14 | 0.19236 | 0.19028 | 0.18889 | 0.18681 | 0.18472 | 0.18264 | 0.18056 | 0.17847 | 0.17569 | 0.17361 | 0.17083 | 0.16875 | 0.16597
| 14.5 | 0.17639 | 0.175 | 0.17292 | 0.17083 | 0.16875 | 0.16667 | 0.16389 | 0.16181 | 0.15972 | 0.15694 | 0.15486 | 0.15208 | 0.15
| 15 | 0.1625 | 0.16042 | 0.15833 | 0.15625 | 0.15417 | 0.15208 | 0.14931 | 0.14722 | 0.14514 | 0.14236 | 0.14028 | 0.1375 | 0.13542
| 15.5 | 0.14931 | 0.14722 | 0.14514 | 0.14306 | 0.14097 | 0.13889 | 0.13681 | 0.13403 | 0.13194 | 0.12917 | 0.12708 | 0.12431 | 0.12153
| 16 | 0.1375 | 0.13542 | 0.13333 | 0.13125 | 0.12917 | 0.12708 | 0.12431 | 0.12222 | 0.11944 | 0.11736 | 0.11458 | 0.1125 | 0.11042
| 16.5 | 0.12708 | 0.125 | 0.12292 | 0.12083 | 0.11806 | 0.11597 | 0.11389 | 0.11111 | 0.10903 | 0.10625 | 0.10417 | 0.10208 | 0.1
| 17 | 0.11736 | 0.11528 | 0.11319 | 0.11042 | 0.10833 | 0.10625 | 0.10347 | 0.10139 | 0.099306 | 0.097222 | 0.095139 | 0.093056 | 0.091667
| 17.5 | 0.10833 | 0.10625 | 0.10347 | 0.10139 | 0.099306 | 0.097222 | 0.095139 | 0.093056 | 0.090972 | 0.088889 | 0.086806 | 0.085417 | 0.083333
| 18 | 0.1 | 0.097917 | 0.095833 | 0.09375 | 0.090972 | 0.088889 | 0.086806 | 0.085417 | 0.083333 | 0.081944 | 0.079861 | 0.078472 | 0.077083
| 18.5 | 0.093056 | 0.090972 | 0.088194 | 0.086111 | 0.084028 | 0.081944 | 0.080556 | 0.078472 | 0.077083 | 0.075694 | 0.074306 | 0.072917 | 0.071528
| 19 | 0.086111 | 0.084028 | 0.081944 | 0.079861 | 0.078472 | 0.076389 | 0.075 | 0.072917 | 0.071528 | 0.070139 | 0.099 | 0.097 | 0.096
| 19.5 | 0.080556 | 0.078472 | 0.076389 | 0.075 | 0.072917 | 0.071528 | 0.070139 | 0.099 | 0.097 | 0.095 | 0.093 | 0.091 | 0.089
| 20 | 0.075694 | 0.073611 | 0.072222 | 0.070139 | 0.099 | 0.097 | 0.095 | 0.093 | 0.091 | 0.089 | 0.087 | 0.086 | 0.084
| 20.5 | 0.071528 | 0.069444 | 0.098 | 0.096 | 0.093 | 0.091 | 0.089 | 0.088 | 0.086 | 0.084 | 0.083 | 0.081 | 0.08
| 21 | 0.097 | 0.095 | 0.093 | 0.091 | 0.089 | 0.087 | 0.085 | 0.083 | 0.082 | 0.08 | 0.079 | 0.077 | 0.076
| 21.5 | 0.093 | 0.09 | 0.088 | 0.086 | 0.085 | 0.083 | 0.081 | 0.079 | 0.078 | 0.076 | 0.075 | 0.074 | 0.072
| 22 | 0.089 | 0.087 | 0.085 | 0.083 | 0.081 | 0.079 | 0.078 | 0.076 | 0.075 | 0.073 | 0.072 | 0.07 | 0.069
| 22.5 | 0.083 | 0.082 | 0.08 | 0.078 | 0.076 | 0.074 | 0.073 | 0.071 | 0.07 | 0.068 | 0.067 | 0.066 | 0.065
| 23 | 0.078 | 0.076 | 0.075 | 0.073 | 0.071 | 0.069 | 0.068 | 0.067 | 0.066 | 0.064 | 0.063 | 0.061 | 0.061
| 23.5 | 0.073 | 0.071 | 0.07 | 0.068 | 0.066 | 0.065 | 0.064 | 0.062 | 0.061 | 0.06 | 0.059 | 0.057 | 0.057
| 24 | 0.068 | 0.067 | 0.065 | 0.064 | 0.062 | 0.061 | 0.06 | 0.058 | 0.058 | 0.056 | 0.055 | 0.054 | 0.053
| 24.5 | 0.064 | 0.063 | 0.061 | 0.06 | 0.058 | 0.057 | 0.056 | 0.055 | 0.054 | 0.052 | 0.052 | 0.05 | 0.05
| 25 | 0.06 | 0.059 | 0.057 | 0.056 | 0.055 | 0.053 | 0.053 | 0.051 | 0.051 | 0.049 | 0.049 | 0.047 | 0.047
| 25.5 | 0.056 | 0.055 | 0.054 | 0.053 | 0.051 | 0.05 | 0.049 | 0.048 | 0.048 | 0.046 | 0.046 | 0.044 | 0.044
| 26 | 0.053 | 0.052 | 0.051 | 0.05 | 0.048 | 0.047 | 0.047 | 0.045 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041
| 26.5 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.044 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039
| 27 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.04 | 0.039 | 0.038 | 0.037 | 0.037
| 27.5 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.038 | 0.038 | 0.037 | 0.036 | 0.035 | 0.035
| 28 | 0.042 | 0.041 | 0.041 | 0.04 | 0.039 | 0.038 | 0.037 | 0.036 | 0.036 | 0.035 | 0.034 | 0.033 | 0.033