## Sheet1
PROPERTIES
General
Name | Nordex N149/4.X Mode 0.ab 4,8MW
Manufacturer | Nordex
Hub Height | 105 | 108 | 125 | 135 | 145 | 155 | 164
Power
Rated Power | 4800
Peak Power | 4800
Power Regulation Type | Pitch
Voltage | 690
Rotor
Rotor diameter | 149
Number of blades | 3
Rated RPM | 12.3
Rotor tilt | 6
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 26
Restart Wind Speed | 25.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 40
High Temperature Restart | 38
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | S
Values
Certification | IEC 3rd Edition
Vave | 7.5-9
Vref | 42
Design TI | 0.11

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 2 | 4 | 5 | 8 | 10 | 12 | 13 | 16 | 18 | 20 | 23 | 24 | 26 | 29 | 31 | 33 | 34
| 3.5 | 9 | 11 | 13 | 14 | 16 | 18 | 19 | 21 | 23 | 24 | 26 | 28 | 29 | 31 | 32 | 34 | 36
| 4 | 77 | 80 | 84 | 87 | 91 | 94 | 98 | 101 | 105 | 108 | 112 | 115 | 119 | 122 | 126 | 129 | 133
| 4.5 | 169 | 175 | 181 | 187 | 193 | 199 | 205 | 211 | 217 | 223 | 229 | 235 | 241 | 247 | 253 | 259 | 265
| 5 | 282 | 291 | 300 | 309 | 318 | 327 | 336 | 346 | 355 | 364 | 373 | 382 | 391 | 400 | 409 | 419 | 428
| 5.5 | 417 | 430 | 443 | 455 | 468 | 481 | 494 | 507 | 520 | 533 | 545 | 558 | 571 | 584 | 597 | 610 | 622
| 6 | 576 | 593 | 611 | 628 | 645 | 662 | 680 | 697 | 714 | 731 | 748 | 766 | 783 | 800 | 817 | 834 | 852
| 6.5 | 763 | 786 | 808 | 831 | 853 | 875 | 898 | 920 | 942 | 964 | 987 | 1009 | 1031 | 1054 | 1076 | 1098 | 1120
| 7 | 982 | 1010 | 1039 | 1067 | 1095 | 1123 | 1152 | 1180 | 1208 | 1236 | 1265 | 1293 | 1321 | 1349 | 1377 | 1405 | 1433
| 7.5 | 1235 | 1271 | 1306 | 1341 | 1376 | 1411 | 1446 | 1481 | 1516 | 1551 | 1586 | 1621 | 1656 | 1691 | 1726 | 1761 | 1796
| 8 | 1526 | 1569 | 1612 | 1655 | 1698 | 1741 | 1784 | 1827 | 1870 | 1912 | 1955 | 1998 | 2040 | 2083 | 2125 | 2168 | 2210
| 8.5 | 1856 | 1908 | 1960 | 2012 | 2064 | 2115 | 2167 | 2218 | 2270 | 2321 | 2373 | 2424 | 2476 | 2527 | 2578 | 2630 | 2680
| 9 | 2228 | 2290 | 2351 | 2413 | 2475 | 2536 | 2597 | 2659 | 2720 | 2781 | 2842 | 2901 | 2959 | 3016 | 3072 | 3127 | 3180
| 9.5 | 2633 | 2706 | 2778 | 2850 | 2922 | 2994 | 3066 | 3138 | 3210 | 3278 | 3343 | 3404 | 3464 | 3520 | 3575 | 3629 | 3680
| 10 | 3051 | 3134 | 3218 | 3301 | 3385 | 3466 | 3546 | 3625 | 3705 | 3770 | 3824 | 3875 | 3923 | 3969 | 4014 | 4057 | 4098
| 10.5 | 3467 | 3562 | 3652 | 3741 | 3829 | 3905 | 3972 | 4038 | 4104 | 4158 | 4199 | 4239 | 4276 | 4311 | 4344 | 4376 | 4405
| 11 | 3861 | 3957 | 4036 | 4110 | 4183 | 4245 | 4299 | 4353 | 4406 | 4447 | 4477 | 4504 | 4529 | 4552 | 4574 | 4594 | 4613
| 11.5 | 4183 | 4263 | 4327 | 4387 | 4446 | 4494 | 4535 | 4575 | 4615 | 4643 | 4660 | 4676 | 4690 | 4703 | 4715 | 4726 | 4736
| 12 | 4422 | 4487 | 4537 | 4581 | 4626 | 4661 | 4688 | 4714 | 4741 | 4757 | 4763 | 4768 | 4774 | 4778 | 4782 | 4786 | 4790
| 12.5 | 4592 | 4641 | 4677 | 4707 | 4737 | 4758 | 4770 | 4783 | 4795 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800
| 13 | 4706 | 4740 | 4760 | 4776 | 4791 | 4798 | 4799 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800
| 13.5 | 4772 | 4790 | 4796 | 4798 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800
| 14 | 4797 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800
| 14.5 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800
| 15 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800
| 15.5 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800
| 16 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800
| 16.5 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800
| 17 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800
| 17.5 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800
| 18 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800
| 18.5 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800
| 19 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800
| 19.5 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800
| 20 | 4761 | 4761 | 4761 | 4761 | 4761 | 4761 | 4761 | 4761 | 4761 | 4761 | 4761 | 4761 | 4761 | 4761 | 4761 | 4761 | 4761
| 20.5 | 4655 | 4655 | 4655 | 4655 | 4655 | 4655 | 4655 | 4655 | 4655 | 4655 | 4655 | 4655 | 4655 | 4655 | 4655 | 4655 | 4655
| 21 | 4482 | 4482 | 4482 | 4482 | 4482 | 4482 | 4482 | 4482 | 4482 | 4482 | 4482 | 4482 | 4482 | 4482 | 4482 | 4482 | 4482
| 21.5 | 4307 | 4307 | 4307 | 4307 | 4307 | 4307 | 4307 | 4307 | 4307 | 4307 | 4307 | 4307 | 4307 | 4307 | 4307 | 4307 | 4307
| 22 | 4131 | 4131 | 4131 | 4131 | 4131 | 4131 | 4131 | 4131 | 4131 | 4131 | 4131 | 4131 | 4131 | 4131 | 4131 | 4131 | 4131
| 22.5 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951
| 23 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776
| 23.5 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600
| 24 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420
| 24.5 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245
| 25 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065
| 25.5 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885
| 26 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705
|  | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431
| 3.5 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361
| 4 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736
| 4.5 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111
| 5 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556
| 5.5 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139
| 6 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931
| 6.5 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792
| 7 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722
| 7.5 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54722 | 0.54722 | 0.54653 | 0.54653 | 0.54583 | 0.54514 | 0.54514 | 0.54444
| 8 | 0.54375 | 0.54375 | 0.54375 | 0.54375 | 0.54375 | 0.54375 | 0.54375 | 0.54375 | 0.54375 | 0.54375 | 0.54375 | 0.54236 | 0.54028 | 0.53819 | 0.53611 | 0.53403 | 0.53194
| 8.5 | 0.53264 | 0.53264 | 0.53264 | 0.53264 | 0.53264 | 0.53264 | 0.53264 | 0.53264 | 0.53264 | 0.53264 | 0.53056 | 0.52708 | 0.52361 | 0.51944 | 0.51597 | 0.51319 | 0.50972
| 9 | 0.51667 | 0.51667 | 0.51667 | 0.51667 | 0.51597 | 0.51597 | 0.51389 | 0.5125 | 0.51111 | 0.50972 | 0.50556 | 0.50139 | 0.49653 | 0.49167 | 0.4875 | 0.48333 | 0.47917
| 9.5 | 0.49653 | 0.49583 | 0.49514 | 0.49306 | 0.49167 | 0.48958 | 0.48681 | 0.48403 | 0.48194 | 0.47917 | 0.475 | 0.46944 | 0.46389 | 0.45903 | 0.45417 | 0.44931 | 0.44514
| 10 | 0.47153 | 0.46944 | 0.46736 | 0.46458 | 0.46181 | 0.45972 | 0.45556 | 0.45208 | 0.44931 | 0.44583 | 0.44097 | 0.43542 | 0.42986 | 0.42431 | 0.41875 | 0.41389 | 0.40903
| 10.5 | 0.44236 | 0.43958 | 0.43681 | 0.43333 | 0.42986 | 0.42708 | 0.42292 | 0.41875 | 0.41458 | 0.41181 | 0.40625 | 0.40069 | 0.39444 | 0.38889 | 0.38333 | 0.37778 | 0.37292
| 11 | 0.41111 | 0.40833 | 0.40486 | 0.40069 | 0.39722 | 0.39375 | 0.38889 | 0.38472 | 0.38056 | 0.37708 | 0.37153 | 0.36528 | 0.35903 | 0.35347 | 0.34792 | 0.34306 | 0.3375
| 11.5 | 0.37986 | 0.37639 | 0.37222 | 0.36806 | 0.36389 | 0.36042 | 0.35556 | 0.35069 | 0.34653 | 0.34306 | 0.3375 | 0.33125 | 0.325 | 0.31944 | 0.31389 | 0.30833 | 0.30347
| 12 | 0.34861 | 0.34444 | 0.34028 | 0.33611 | 0.33125 | 0.32778 | 0.32292 | 0.31806 | 0.31389 | 0.30972 | 0.30417 | 0.29792 | 0.29167 | 0.28542 | 0.27986 | 0.275 | 0.26944
| 12.5 | 0.31736 | 0.31319 | 0.30903 | 0.30417 | 0.3 | 0.29583 | 0.29097 | 0.28611 | 0.28125 | 0.27708 | 0.27153 | 0.26597 | 0.25972 | 0.25417 | 0.24861 | 0.24306 | 0.23819
| 13 | 0.2875 | 0.28333 | 0.27917 | 0.27361 | 0.26944 | 0.26528 | 0.25972 | 0.25556 | 0.25069 | 0.24653 | 0.24097 | 0.23542 | 0.22986 | 0.22431 | 0.21944 | 0.21458 | 0.21042
| 13.5 | 0.25972 | 0.25486 | 0.25069 | 0.24583 | 0.24097 | 0.23681 | 0.23194 | 0.22708 | 0.22222 | 0.21806 | 0.2125 | 0.20764 | 0.20278 | 0.19792 | 0.19375 | 0.18958 | 0.18542
| 14 | 0.23472 | 0.22986 | 0.22569 | 0.22083 | 0.21597 | 0.21181 | 0.20625 | 0.20139 | 0.19722 | 0.19306 | 0.18819 | 0.18333 | 0.17917 | 0.175 | 0.17083 | 0.16736 | 0.16389
| 14.5 | 0.21181 | 0.20694 | 0.20278 | 0.19792 | 0.19306 | 0.18889 | 0.18333 | 0.17917 | 0.17431 | 0.17014 | 0.16597 | 0.1625 | 0.15903 | 0.15556 | 0.15208 | 0.14931 | 0.14653
| 15 | 0.19097 | 0.18681 | 0.18194 | 0.17708 | 0.17222 | 0.16806 | 0.16389 | 0.15972 | 0.15556 | 0.15208 | 0.14861 | 0.14514 | 0.14236 | 0.13958 | 0.13681 | 0.13403 | 0.13125
| 15.5 | 0.17222 | 0.16806 | 0.16319 | 0.15903 | 0.15417 | 0.15069 | 0.14653 | 0.14306 | 0.14028 | 0.13681 | 0.13403 | 0.13125 | 0.12847 | 0.12569 | 0.12292 | 0.12083 | 0.11875
| 16 | 0.15556 | 0.15139 | 0.14722 | 0.14306 | 0.13958 | 0.13611 | 0.13264 | 0.12917 | 0.12639 | 0.12361 | 0.12083 | 0.11875 | 0.11597 | 0.11389 | 0.11181 | 0.10972 | 0.10764
| 16.5 | 0.14097 | 0.13681 | 0.13333 | 0.12986 | 0.12639 | 0.12361 | 0.12083 | 0.11806 | 0.11528 | 0.1125 | 0.11042 | 0.10833 | 0.10625 | 0.10417 | 0.10208 | 0.1 | 0.098611
| 17 | 0.12917 | 0.12569 | 0.12222 | 0.11875 | 0.11597 | 0.11319 | 0.11042 | 0.10833 | 0.10556 | 0.10347 | 0.10139 | 0.099306 | 0.097222 | 0.095833 | 0.09375 | 0.092361 | 0.090278
| 17.5 | 0.11875 | 0.11528 | 0.1125 | 0.10972 | 0.10694 | 0.10486 | 0.10208 | 0.1 | 0.097917 | 0.095833 | 0.09375 | 0.091667 | 0.090278 | 0.088194 | 0.086806 | 0.085417 | 0.084028
| 18 | 0.11042 | 0.10764 | 0.10486 | 0.10208 | 0.099306 | 0.097222 | 0.095139 | 0.093056 | 0.090972 | 0.088889 | 0.0875 | 0.085417 | 0.084028 | 0.082639 | 0.08125 | 0.079167 | 0.077778
| 18.5 | 0.10278 | 0.1 | 0.097917 | 0.095139 | 0.093056 | 0.090972 | 0.088889 | 0.086806 | 0.085417 | 0.083333 | 0.081944 | 0.080556 | 0.078472 | 0.077083 | 0.075694 | 0.074306 | 0.073611
| 19 | 0.097222 | 0.094444 | 0.092361 | 0.089583 | 0.0875 | 0.085417 | 0.084028 | 0.081944 | 0.080556 | 0.078472 | 0.077083 | 0.075694 | 0.074306 | 0.072917 | 0.071528 | 0.070139 | 0.069444
| 19.5 | 0.091667 | 0.089583 | 0.0875 | 0.085417 | 0.083333 | 0.08125 | 0.079167 | 0.077778 | 0.076389 | 0.075 | 0.072917 | 0.071528 | 0.070139 | 0.069444 | 0.098 | 0.096 | 0.095
| 20 | 0.0875 | 0.085417 | 0.083333 | 0.08125 | 0.079167 | 0.077778 | 0.075694 | 0.074306 | 0.072917 | 0.071528 | 0.070139 | 0.099 | 0.097 | 0.095 | 0.093 | 0.092 | 0.09
| 20.5 | 0.080556 | 0.079167 | 0.077083 | 0.075 | 0.072917 | 0.071528 | 0.070139 | 0.099 | 0.097 | 0.095 | 0.093 | 0.091 | 0.09 | 0.088 | 0.086 | 0.085 | 0.083
| 21 | 0.073611 | 0.071528 | 0.070139 | 0.098 | 0.096 | 0.094 | 0.091 | 0.09 | 0.088 | 0.086 | 0.085 | 0.083 | 0.081 | 0.08 | 0.078 | 0.077 | 0.076
| 21.5 | 0.095 | 0.092 | 0.09 | 0.088 | 0.086 | 0.084 | 0.082 | 0.08 | 0.079 | 0.077 | 0.076 | 0.074 | 0.073 | 0.071 | 0.07 | 0.069 | 0.068
| 22 | 0.085 | 0.083 | 0.081 | 0.079 | 0.077 | 0.076 | 0.074 | 0.072 | 0.071 | 0.07 | 0.068 | 0.067 | 0.066 | 0.064 | 0.063 | 0.062 | 0.061
| 22.5 | 0.076 | 0.075 | 0.073 | 0.071 | 0.069 | 0.068 | 0.066 | 0.065 | 0.064 | 0.062 | 0.061 | 0.06 | 0.059 | 0.058 | 0.056 | 0.056 | 0.055
| 23 | 0.069 | 0.067 | 0.066 | 0.064 | 0.062 | 0.061 | 0.06 | 0.058 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049
| 23.5 | 0.061 | 0.06 | 0.059 | 0.057 | 0.056 | 0.055 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.045 | 0.044
| 24 | 0.055 | 0.054 | 0.053 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.04
| 24.5 | 0.05 | 0.049 | 0.048 | 0.047 | 0.045 | 0.045 | 0.043 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.038 | 0.037 | 0.037 | 0.036
| 25 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.038 | 0.037 | 0.036 | 0.036 | 0.035 | 0.034 | 0.034 | 0.033 | 0.032
| 25.5 | 0.041 | 0.04 | 0.039 | 0.038 | 0.037 | 0.036 | 0.035 | 0.035 | 0.034 | 0.033 | 0.033 | 0.032 | 0.031 | 0.031 | 0.03 | 0.03 | 0.029
| 26 | 0.037 | 0.036 | 0.035 | 0.035 | 0.034 | 0.033 | 0.032 | 0.032 | 0.031 | 0.03 | 0.03 | 0.029 | 0.029 | 0.028 | 0.027 | 0.027 | 0.027