## Sheet1
PROPERTIES
General
Name | Nordex N149/4.X Mode 0.b 4,5MW
Manufacturer | Nordex
Hub Height | 105 | 108 | 125 | 135 | 145 | 155 | 164
Power
Rated Power | 4500
Peak Power | 4500
Power Regulation Type | Pitch
Voltage | 660
Rotor
Rotor diameter | 149
Number of blades | 3
Rated RPM | 12.3
Rotor tilt | 6
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 26
Restart Wind Speed | 25.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 40
High Temperature Restart | 38
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | S
Values
Certification | IEC 3rd Edition
Vave | 7.5-9
Vref | 42
Design TI | 0.11

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 9 | 11 | 13 | 14 | 16 | 18 | 19 | 21 | 23 | 24 | 26 | 28 | 29 | 31 | 32 | 34 | 36
| 3.5 | 77 | 80 | 84 | 87 | 91 | 94 | 98 | 101 | 105 | 108 | 112 | 115 | 119 | 122 | 126 | 129 | 133
| 4 | 169 | 175 | 181 | 187 | 193 | 199 | 205 | 211 | 217 | 223 | 229 | 235 | 241 | 247 | 253 | 259 | 265
| 4.5 | 282 | 291 | 300 | 309 | 318 | 327 | 336 | 346 | 355 | 364 | 373 | 382 | 391 | 400 | 409 | 419 | 428
| 5 | 417 | 430 | 443 | 455 | 468 | 481 | 494 | 507 | 520 | 533 | 545 | 558 | 571 | 584 | 597 | 610 | 622
| 5.5 | 576 | 593 | 611 | 628 | 645 | 662 | 680 | 697 | 714 | 731 | 748 | 766 | 783 | 800 | 817 | 834 | 852
| 6 | 763 | 786 | 808 | 831 | 853 | 875 | 898 | 920 | 942 | 964 | 987 | 1009 | 1031 | 1054 | 1076 | 1098 | 1120
| 6.5 | 982 | 1010 | 1039 | 1067 | 1095 | 1124 | 1152 | 1180 | 1208 | 1236 | 1265 | 1293 | 1321 | 1349 | 1377 | 1405 | 1433
| 7 | 1235 | 1271 | 1306 | 1341 | 1376 | 1411 | 1446 | 1481 | 1516 | 1551 | 1586 | 1621 | 1656 | 1691 | 1726 | 1761 | 1796
| 7.5 | 1526 | 1569 | 1612 | 1655 | 1698 | 1741 | 1784 | 1827 | 1870 | 1912 | 1955 | 1998 | 2040 | 2083 | 2125 | 2168 | 2210
| 8 | 1856 | 1908 | 1960 | 2012 | 2064 | 2115 | 2167 | 2219 | 2270 | 2322 | 2373 | 2424 | 2476 | 2527 | 2578 | 2629 | 2680
| 8.5 | 2228 | 2290 | 2351 | 2413 | 2475 | 2536 | 2597 | 2659 | 2720 | 2781 | 2842 | 2901 | 2959 | 3016 | 3072 | 3127 | 3180
| 9 | 2633 | 2705 | 2778 | 2850 | 2923 | 2995 | 3066 | 3137 | 3207 | 3275 | 3339 | 3401 | 3458 | 3506 | 3553 | 3600 | 3644
| 9.5 | 3051 | 3135 | 3218 | 3299 | 3379 | 3458 | 3530 | 3590 | 3649 | 3706 | 3759 | 3810 | 3857 | 3894 | 3930 | 3966 | 3999
| 10 | 3462 | 3551 | 3635 | 3702 | 3769 | 3836 | 3894 | 3942 | 3990 | 4035 | 4077 | 4116 | 4151 | 4177 | 4203 | 4227 | 4250
| 10.5 | 3816 | 3890 | 3960 | 4014 | 4068 | 4121 | 4167 | 4203 | 4238 | 4271 | 4301 | 4328 | 4351 | 4367 | 4381 | 4394 | 4407
| 11 | 4083 | 4142 | 4199 | 4239 | 4279 | 4319 | 4352 | 4376 | 4399 | 4419 | 4437 | 4453 | 4465 | 4470 | 4474 | 4478 | 4481
| 11.5 | 4273 | 4318 | 4360 | 4387 | 4414 | 4441 | 4460 | 4470 | 4479 | 4487 | 4493 | 4498 | 4500 | 4500 | 4500 | 4500 | 4500
| 12 | 4398 | 4429 | 4456 | 4468 | 4481 | 4493 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
| 12.5 | 4470 | 4485 | 4498 | 4499 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
| 13 | 4498 | 4499 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
| 13.5 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
| 14 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
| 14.5 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
| 15 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
| 15.5 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
| 16 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
| 16.5 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
| 17 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
| 17.5 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
| 18 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
| 18.5 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
| 19 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
| 19.5 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
| 20 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
| 20.5 | 4455 | 4455 | 4455 | 4455 | 4455 | 4455 | 4455 | 4455 | 4455 | 4455 | 4455 | 4455 | 4455 | 4455 | 4455 | 4455 | 4455
| 21 | 4307 | 4307 | 4307 | 4307 | 4307 | 4307 | 4307 | 4307 | 4307 | 4307 | 4307 | 4307 | 4307 | 4307 | 4307 | 4307 | 4307
| 21.5 | 4131 | 4131 | 4131 | 4131 | 4131 | 4131 | 4131 | 4131 | 4131 | 4131 | 4131 | 4131 | 4131 | 4131 | 4131 | 4131 | 4131
| 22 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951
| 22.5 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776
| 23 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600
| 23.5 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420
| 24 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245
| 24.5 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065
| 25 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885
| 25.5 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705
| 26 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431
| 3.5 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361
| 4 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736
| 4.5 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111
| 5 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556
| 5.5 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139
| 6 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931
| 6.5 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792
| 7 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722
| 7.5 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54722 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54583 | 0.54583 | 0.54514 | 0.54514 | 0.54444
| 8 | 0.54375 | 0.54375 | 0.54375 | 0.54375 | 0.54375 | 0.54375 | 0.54375 | 0.54375 | 0.54375 | 0.54375 | 0.54375 | 0.54236 | 0.54028 | 0.5375 | 0.53472 | 0.53264 | 0.52986
| 8.5 | 0.53264 | 0.53264 | 0.53264 | 0.53264 | 0.53264 | 0.53264 | 0.53264 | 0.53125 | 0.52917 | 0.52778 | 0.52569 | 0.52292 | 0.51944 | 0.51458 | 0.51042 | 0.50694 | 0.50347
| 9 | 0.51667 | 0.51597 | 0.51597 | 0.51458 | 0.5125 | 0.51111 | 0.50972 | 0.50625 | 0.50347 | 0.50069 | 0.49722 | 0.49375 | 0.48889 | 0.48333 | 0.47917 | 0.47431 | 0.47014
| 9.5 | 0.49444 | 0.49236 | 0.49028 | 0.48819 | 0.48472 | 0.48194 | 0.47917 | 0.475 | 0.47153 | 0.46806 | 0.46389 | 0.45972 | 0.45417 | 0.44861 | 0.44375 | 0.43889 | 0.43403
| 10 | 0.46597 | 0.46319 | 0.46042 | 0.45694 | 0.45278 | 0.44931 | 0.44653 | 0.44167 | 0.43681 | 0.43333 | 0.42917 | 0.42431 | 0.41875 | 0.4125 | 0.40694 | 0.40208 | 0.39722
| 10.5 | 0.43472 | 0.43125 | 0.42778 | 0.42361 | 0.41944 | 0.41528 | 0.41181 | 0.40694 | 0.40208 | 0.39722 | 0.39306 | 0.38819 | 0.38194 | 0.37639 | 0.37083 | 0.36528 | 0.36042
| 11 | 0.40278 | 0.39861 | 0.39444 | 0.39028 | 0.38542 | 0.38125 | 0.37708 | 0.37222 | 0.36667 | 0.3625 | 0.35764 | 0.35278 | 0.34653 | 0.34028 | 0.33472 | 0.32986 | 0.32431
| 11.5 | 0.37014 | 0.36597 | 0.36181 | 0.35694 | 0.35208 | 0.34722 | 0.34306 | 0.3375 | 0.33264 | 0.32778 | 0.32292 | 0.31806 | 0.31181 | 0.30556 | 0.3 | 0.29514 | 0.28958
| 12 | 0.33819 | 0.33333 | 0.32917 | 0.32431 | 0.31875 | 0.31458 | 0.30972 | 0.30417 | 0.29931 | 0.29444 | 0.28958 | 0.28403 | 0.27847 | 0.27222 | 0.26667 | 0.26111 | 0.25625
| 12.5 | 0.30694 | 0.30208 | 0.29722 | 0.29236 | 0.28681 | 0.28194 | 0.27778 | 0.27222 | 0.26736 | 0.2625 | 0.25764 | 0.25208 | 0.24653 | 0.24028 | 0.23472 | 0.22917 | 0.22431
| 13 | 0.27639 | 0.27153 | 0.26667 | 0.26181 | 0.25625 | 0.25139 | 0.24722 | 0.24167 | 0.23611 | 0.23125 | 0.22639 | 0.22153 | 0.21597 | 0.21042 | 0.20556 | 0.20139 | 0.19653
| 13.5 | 0.24861 | 0.24306 | 0.23819 | 0.23333 | 0.22778 | 0.22292 | 0.21875 | 0.21319 | 0.20764 | 0.20278 | 0.19792 | 0.19375 | 0.18889 | 0.18472 | 0.18056 | 0.17639 | 0.17292
| 14 | 0.22292 | 0.21806 | 0.21319 | 0.20764 | 0.20278 | 0.19792 | 0.19306 | 0.18819 | 0.18333 | 0.17847 | 0.17431 | 0.17014 | 0.16667 | 0.1625 | 0.15972 | 0.15625 | 0.15347
| 14.5 | 0.2 | 0.19514 | 0.19028 | 0.18542 | 0.17986 | 0.175 | 0.17083 | 0.16667 | 0.1625 | 0.15833 | 0.15486 | 0.15139 | 0.14792 | 0.14514 | 0.14236 | 0.13958 | 0.13681
| 15 | 0.17986 | 0.17431 | 0.16944 | 0.16528 | 0.16042 | 0.15625 | 0.15208 | 0.14861 | 0.14514 | 0.14167 | 0.13889 | 0.13611 | 0.13333 | 0.13056 | 0.12778 | 0.12569 | 0.12292
| 15.5 | 0.16111 | 0.15625 | 0.15208 | 0.14792 | 0.14375 | 0.14028 | 0.13681 | 0.13403 | 0.13056 | 0.12778 | 0.125 | 0.12292 | 0.12014 | 0.11806 | 0.11528 | 0.11319 | 0.11111
| 16 | 0.14514 | 0.14097 | 0.13681 | 0.13333 | 0.12986 | 0.12708 | 0.12431 | 0.12083 | 0.11875 | 0.11597 | 0.11319 | 0.11111 | 0.10903 | 0.10694 | 0.10486 | 0.10278 | 0.10139
| 16.5 | 0.13194 | 0.12778 | 0.125 | 0.12153 | 0.11875 | 0.11597 | 0.11319 | 0.11042 | 0.10833 | 0.10556 | 0.10347 | 0.10139 | 0.099306 | 0.097917 | 0.095833 | 0.094444 | 0.092361
| 17 | 0.12083 | 0.11736 | 0.11458 | 0.11111 | 0.10903 | 0.10625 | 0.10347 | 0.10139 | 0.099306 | 0.097222 | 0.095139 | 0.093056 | 0.091667 | 0.089583 | 0.088194 | 0.086806 | 0.085417
| 17.5 | 0.11111 | 0.10833 | 0.10556 | 0.10278 | 0.10069 | 0.097917 | 0.095833 | 0.09375 | 0.091667 | 0.090278 | 0.088194 | 0.086111 | 0.084722 | 0.083333 | 0.081944 | 0.080556 | 0.079167
| 18 | 0.10347 | 0.10069 | 0.097917 | 0.095833 | 0.09375 | 0.090972 | 0.089583 | 0.0875 | 0.085417 | 0.084028 | 0.081944 | 0.080556 | 0.079167 | 0.077778 | 0.076389 | 0.075 | 0.073611
| 18.5 | 0.096528 | 0.094444 | 0.091667 | 0.089583 | 0.0875 | 0.085417 | 0.083333 | 0.081944 | 0.079861 | 0.078472 | 0.077083 | 0.075694 | 0.074306 | 0.072917 | 0.071528 | 0.070139 | 0.069444
| 19 | 0.090972 | 0.088889 | 0.086111 | 0.084722 | 0.082639 | 0.080556 | 0.079167 | 0.077083 | 0.075694 | 0.074306 | 0.072917 | 0.071528 | 0.070139 | 0.099 | 0.097 | 0.096 | 0.094
| 19.5 | 0.086111 | 0.084028 | 0.081944 | 0.079861 | 0.078472 | 0.076389 | 0.075 | 0.072917 | 0.071528 | 0.070139 | 0.099 | 0.097 | 0.096 | 0.094 | 0.092 | 0.091 | 0.089
| 20 | 0.081944 | 0.079861 | 0.077778 | 0.076389 | 0.074306 | 0.072917 | 0.071528 | 0.070139 | 0.099 | 0.097 | 0.095 | 0.093 | 0.091 | 0.09 | 0.088 | 0.087 | 0.085
| 20.5 | 0.075694 | 0.073611 | 0.071528 | 0.070833 | 0.099 | 0.097 | 0.095 | 0.093 | 0.091 | 0.09 | 0.088 | 0.086 | 0.084 | 0.083 | 0.081 | 0.08 | 0.078
| 21 | 0.099 | 0.096 | 0.094 | 0.092 | 0.09 | 0.088 | 0.086 | 0.085 | 0.083 | 0.081 | 0.08 | 0.078 | 0.076 | 0.076 | 0.074 | 0.073 | 0.071
| 21.5 | 0.089 | 0.086 | 0.084 | 0.083 | 0.08 | 0.079 | 0.077 | 0.076 | 0.074 | 0.073 | 0.071 | 0.07 | 0.068 | 0.068 | 0.066 | 0.065 | 0.064
| 22 | 0.08 | 0.078 | 0.076 | 0.074 | 0.072 | 0.071 | 0.07 | 0.068 | 0.067 | 0.066 | 0.064 | 0.063 | 0.062 | 0.061 | 0.06 | 0.059 | 0.058
| 22.5 | 0.072 | 0.07 | 0.068 | 0.067 | 0.065 | 0.064 | 0.062 | 0.061 | 0.06 | 0.059 | 0.058 | 0.056 | 0.055 | 0.055 | 0.053 | 0.053 | 0.052
| 23 | 0.064 | 0.063 | 0.061 | 0.06 | 0.058 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.048 | 0.046
| 23.5 | 0.058 | 0.056 | 0.055 | 0.054 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.044 | 0.043 | 0.042 | 0.041
| 24 | 0.052 | 0.051 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.04 | 0.039 | 0.038 | 0.037
| 24.5 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.038 | 0.037 | 0.036 | 0.036 | 0.035 | 0.035 | 0.034
| 25 | 0.043 | 0.042 | 0.04 | 0.04 | 0.039 | 0.038 | 0.037 | 0.036 | 0.036 | 0.035 | 0.034 | 0.034 | 0.033 | 0.032 | 0.032 | 0.031 | 0.031
| 25.5 | 0.038 | 0.037 | 0.036 | 0.036 | 0.035 | 0.034 | 0.033 | 0.033 | 0.032 | 0.031 | 0.031 | 0.03 | 0.029 | 0.029 | 0.028 | 0.028 | 0.027
| 26 | 0.035 | 0.034 | 0.033 | 0.032 | 0.032 | 0.031 | 0.03 | 0.03 | 0.029 | 0.029 | 0.028 | 0.027 | 0.027 | 0.027 | 0.026 | 0.026 | 0.025