## Sheet1
PROPERTIES
General
Name | Nordex N149/4.X Mode 2.a 4,5MW
Manufacturer | Nordex
Hub Height | 105 | 108 | 125 | 135 | 145 | 155 | 164
Power
Rated Power | 4500
Peak Power | 4500
Power Regulation Type | Pitch
Voltage | 660
Rotor
Rotor diameter | 149
Number of blades | 3
Rated RPM | 12.3
Rotor tilt | 6
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 26
Restart Wind Speed | 25.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 40
High Temperature Restart | 38
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | S
Values
Certification | IEC 3rd Edition
Vave | 7.5-9
Vref | 42
Design TI | 0.11

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 9 | 11 | 13 | 14 | 16 | 18 | 19 | 21 | 23 | 24 | 26 | 28 | 29 | 31 | 32 | 34 | 36
| 3.5 | 77 | 80 | 84 | 87 | 91 | 94 | 98 | 101 | 105 | 108 | 112 | 115 | 119 | 122 | 126 | 129 | 133
| 4 | 169 | 175 | 181 | 187 | 193 | 199 | 205 | 211 | 217 | 223 | 229 | 235 | 241 | 247 | 253 | 259 | 265
| 4.5 | 282 | 291 | 300 | 309 | 318 | 327 | 336 | 346 | 355 | 364 | 373 | 382 | 391 | 400 | 409 | 419 | 428
| 5 | 417 | 430 | 443 | 455 | 468 | 481 | 494 | 507 | 520 | 533 | 545 | 558 | 571 | 584 | 597 | 610 | 622
| 5.5 | 576 | 593 | 611 | 628 | 645 | 662 | 680 | 697 | 714 | 731 | 748 | 766 | 783 | 800 | 817 | 834 | 852
| 6 | 763 | 786 | 808 | 831 | 853 | 875 | 898 | 920 | 942 | 964 | 987 | 1009 | 1031 | 1054 | 1076 | 1098 | 1120
| 6.5 | 982 | 1010 | 1039 | 1067 | 1095 | 1123 | 1152 | 1180 | 1208 | 1236 | 1265 | 1293 | 1321 | 1349 | 1377 | 1405 | 1433
| 7 | 1235 | 1271 | 1306 | 1341 | 1376 | 1411 | 1446 | 1481 | 1516 | 1551 | 1586 | 1621 | 1656 | 1691 | 1726 | 1761 | 1796
| 7.5 | 1526 | 1569 | 1612 | 1655 | 1698 | 1741 | 1784 | 1827 | 1869 | 1912 | 1955 | 1998 | 2041 | 2084 | 2126 | 2168 | 2209
| 8 | 1857 | 1908 | 1960 | 2012 | 2064 | 2116 | 2167 | 2219 | 2270 | 2321 | 2371 | 2420 | 2468 | 2516 | 2562 | 2607 | 2650
| 8.5 | 2221 | 2282 | 2344 | 2405 | 2467 | 2528 | 2589 | 2650 | 2707 | 2761 | 2814 | 2864 | 2912 | 2959 | 3004 | 3047 | 3088
| 9 | 2599 | 2671 | 2742 | 2813 | 2885 | 2956 | 3027 | 3094 | 3151 | 3205 | 3256 | 3304 | 3349 | 3393 | 3434 | 3473 | 3510
| 9.5 | 2975 | 3056 | 3138 | 3220 | 3301 | 3380 | 3458 | 3526 | 3579 | 3628 | 3674 | 3714 | 3749 | 3783 | 3814 | 3843 | 3870
| 10 | 3341 | 3432 | 3520 | 3606 | 3691 | 3762 | 3827 | 3882 | 3923 | 3961 | 3996 | 4024 | 4049 | 4071 | 4092 | 4112 | 4130
| 10.5 | 3681 | 3773 | 3851 | 3922 | 3993 | 4050 | 4102 | 4145 | 4174 | 4200 | 4224 | 4243 | 4259 | 4273 | 4286 | 4298 | 4309
| 11 | 3957 | 4033 | 4097 | 4154 | 4211 | 4254 | 4293 | 4322 | 4341 | 4358 | 4374 | 4385 | 4394 | 4402 | 4409 | 4416 | 4422
| 11.5 | 4163 | 4224 | 4273 | 4316 | 4358 | 4389 | 4414 | 4432 | 4443 | 4453 | 4462 | 4468 | 4471 | 4474 | 4477 | 4479 | 4482
| 12 | 4311 | 4358 | 4393 | 4422 | 4450 | 4467 | 4479 | 4486 | 4491 | 4495 | 4499 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
| 12.5 | 4412 | 4444 | 4465 | 4479 | 4494 | 4499 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
| 13 | 4472 | 4489 | 4497 | 4499 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
| 13.5 | 4497 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
| 14 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
| 14.5 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
| 15 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
| 15.5 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
| 16 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
| 16.5 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
| 17 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
| 17.5 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
| 18 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
| 18.5 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
| 19 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
| 19.5 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
| 20 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
| 20.5 | 4455 | 4455 | 4455 | 4455 | 4455 | 4455 | 4455 | 4455 | 4455 | 4455 | 4455 | 4455 | 4455 | 4455 | 4455 | 4455 | 4455
| 21 | 4307 | 4307 | 4307 | 4307 | 4307 | 4307 | 4307 | 4307 | 4307 | 4307 | 4307 | 4307 | 4307 | 4307 | 4307 | 4307 | 4307
| 21.5 | 4131 | 4131 | 4131 | 4131 | 4131 | 4131 | 4131 | 4131 | 4131 | 4131 | 4131 | 4131 | 4131 | 4131 | 4131 | 4131 | 4131
| 22 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951
| 22.5 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776
| 23 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600
| 23.5 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420
| 24 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245
| 24.5 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065
| 25 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885
| 25.5 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705
| 26 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431
| 3.5 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361
| 4 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736
| 4.5 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111
| 5 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556
| 5.5 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139
| 6 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931
| 6.5 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792
| 7 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54653 | 0.54653 | 0.54653 | 0.54583 | 0.54514 | 0.54375
| 7.5 | 0.54514 | 0.54514 | 0.54514 | 0.54514 | 0.54514 | 0.54514 | 0.54514 | 0.54514 | 0.54514 | 0.54444 | 0.54236 | 0.54028 | 0.53889 | 0.53681 | 0.53472 | 0.53264 | 0.52986
| 8 | 0.53403 | 0.53403 | 0.53403 | 0.53403 | 0.53403 | 0.53472 | 0.53403 | 0.53403 | 0.53403 | 0.53194 | 0.52917 | 0.52569 | 0.52222 | 0.51944 | 0.51667 | 0.51319 | 0.50903
| 8.5 | 0.51736 | 0.51736 | 0.51736 | 0.51736 | 0.51736 | 0.51736 | 0.51736 | 0.51736 | 0.51667 | 0.51389 | 0.50903 | 0.50486 | 0.5 | 0.49583 | 0.49167 | 0.4875 | 0.48264
| 9 | 0.49653 | 0.49653 | 0.49653 | 0.49653 | 0.49653 | 0.49583 | 0.49444 | 0.49306 | 0.49097 | 0.48681 | 0.48125 | 0.47639 | 0.47083 | 0.46597 | 0.46111 | 0.45556 | 0.45
| 9.5 | 0.47292 | 0.47222 | 0.47222 | 0.47083 | 0.46875 | 0.46736 | 0.46528 | 0.4625 | 0.45972 | 0.45486 | 0.44861 | 0.44306 | 0.43681 | 0.43125 | 0.42639 | 0.42083 | 0.41528
| 10 | 0.44583 | 0.44444 | 0.44236 | 0.44028 | 0.43819 | 0.43542 | 0.43264 | 0.42917 | 0.42569 | 0.42083 | 0.41389 | 0.40764 | 0.40208 | 0.39583 | 0.39028 | 0.38472 | 0.37847
| 10.5 | 0.41597 | 0.41319 | 0.41111 | 0.40764 | 0.40486 | 0.40208 | 0.39861 | 0.39514 | 0.39097 | 0.38542 | 0.37917 | 0.37222 | 0.36597 | 0.36042 | 0.35486 | 0.34861 | 0.34236
| 11 | 0.38403 | 0.38125 | 0.37847 | 0.375 | 0.37153 | 0.36806 | 0.36458 | 0.36042 | 0.35625 | 0.35069 | 0.34375 | 0.3375 | 0.33125 | 0.325 | 0.31944 | 0.31319 | 0.30764
| 11.5 | 0.35278 | 0.34931 | 0.34583 | 0.34236 | 0.33819 | 0.33472 | 0.33056 | 0.32639 | 0.32222 | 0.31667 | 0.30972 | 0.30347 | 0.29653 | 0.29097 | 0.28472 | 0.27917 | 0.27361
| 12 | 0.32083 | 0.31736 | 0.31389 | 0.30972 | 0.30556 | 0.30208 | 0.29792 | 0.29375 | 0.28958 | 0.28333 | 0.27708 | 0.27083 | 0.26458 | 0.25833 | 0.25278 | 0.24792 | 0.24306
| 12.5 | 0.29028 | 0.28681 | 0.28264 | 0.27847 | 0.275 | 0.27083 | 0.26667 | 0.2625 | 0.25764 | 0.25208 | 0.24583 | 0.24028 | 0.23472 | 0.22986 | 0.225 | 0.22014 | 0.21597
| 13 | 0.2625 | 0.25903 | 0.25486 | 0.25069 | 0.24653 | 0.24236 | 0.23819 | 0.23403 | 0.22917 | 0.22361 | 0.21875 | 0.21389 | 0.20903 | 0.20417 | 0.2 | 0.19583 | 0.19167
| 13.5 | 0.2375 | 0.23333 | 0.22986 | 0.22569 | 0.22083 | 0.21736 | 0.2125 | 0.20833 | 0.20417 | 0.19931 | 0.19444 | 0.19028 | 0.18542 | 0.18194 | 0.17778 | 0.17431 | 0.17083
| 14 | 0.21528 | 0.21111 | 0.20694 | 0.20278 | 0.19861 | 0.19444 | 0.18958 | 0.18542 | 0.18125 | 0.17708 | 0.17292 | 0.16875 | 0.16528 | 0.16181 | 0.15833 | 0.15486 | 0.15139
| 14.5 | 0.19444 | 0.19028 | 0.18681 | 0.18194 | 0.17778 | 0.17361 | 0.16944 | 0.16528 | 0.16111 | 0.15764 | 0.15347 | 0.15 | 0.14722 | 0.14375 | 0.14097 | 0.13819 | 0.13542
| 15 | 0.17639 | 0.17222 | 0.16806 | 0.16389 | 0.15903 | 0.15556 | 0.15139 | 0.14792 | 0.14444 | 0.14097 | 0.1375 | 0.13472 | 0.13194 | 0.12917 | 0.12639 | 0.12431 | 0.12153
| 15.5 | 0.15972 | 0.15556 | 0.15139 | 0.14722 | 0.14306 | 0.13958 | 0.13611 | 0.13264 | 0.12986 | 0.12708 | 0.12431 | 0.12153 | 0.11875 | 0.11667 | 0.11458 | 0.1125 | 0.11042
| 16 | 0.14444 | 0.14028 | 0.13611 | 0.13264 | 0.12917 | 0.12639 | 0.12292 | 0.12014 | 0.11736 | 0.11458 | 0.1125 | 0.11042 | 0.10764 | 0.10556 | 0.10347 | 0.10208 | 0.1
| 16.5 | 0.13125 | 0.12708 | 0.12361 | 0.12083 | 0.11736 | 0.11458 | 0.11181 | 0.10972 | 0.10694 | 0.10486 | 0.10278 | 0.10069 | 0.098611 | 0.096528 | 0.095139 | 0.093056 | 0.091667
| 17 | 0.12014 | 0.11667 | 0.11319 | 0.11042 | 0.10764 | 0.10556 | 0.10278 | 0.10069 | 0.098611 | 0.096528 | 0.094444 | 0.092361 | 0.090278 | 0.088889 | 0.0875 | 0.085417 | 0.084028
| 17.5 | 0.11042 | 0.10764 | 0.10486 | 0.10208 | 0.1 | 0.097222 | 0.095139 | 0.093056 | 0.090972 | 0.088889 | 0.0875 | 0.085417 | 0.084028 | 0.082639 | 0.080556 | 0.079167 | 0.077778
| 18 | 0.10278 | 0.1 | 0.097222 | 0.095139 | 0.092361 | 0.090278 | 0.088194 | 0.086806 | 0.084722 | 0.082639 | 0.08125 | 0.079861 | 0.078472 | 0.077083 | 0.075694 | 0.074306 | 0.072917
| 18.5 | 0.095833 | 0.09375 | 0.090972 | 0.088889 | 0.086806 | 0.084722 | 0.082639 | 0.08125 | 0.079167 | 0.077778 | 0.076389 | 0.075 | 0.073611 | 0.072222 | 0.070833 | 0.069444 | 0.098
| 19 | 0.090278 | 0.088194 | 0.086111 | 0.084028 | 0.081944 | 0.079861 | 0.078472 | 0.076389 | 0.075 | 0.073611 | 0.072222 | 0.070833 | 0.069444 | 0.098 | 0.096 | 0.094 | 0.093
| 19.5 | 0.085417 | 0.083333 | 0.08125 | 0.079167 | 0.077778 | 0.075694 | 0.074306 | 0.072222 | 0.070833 | 0.069444 | 0.098 | 0.096 | 0.095 | 0.093 | 0.091 | 0.09 | 0.088
| 20 | 0.08125 | 0.079167 | 0.077778 | 0.075694 | 0.073611 | 0.072222 | 0.070833 | 0.069444 | 0.098 | 0.096 | 0.094 | 0.092 | 0.09 | 0.089 | 0.087 | 0.086 | 0.084
| 20.5 | 0.075 | 0.072917 | 0.071528 | 0.070139 | 0.098 | 0.096 | 0.094 | 0.092 | 0.09 | 0.089 | 0.087 | 0.085 | 0.083 | 0.082 | 0.08 | 0.079 | 0.078
| 21 | 0.098 | 0.096 | 0.094 | 0.091 | 0.089 | 0.087 | 0.086 | 0.084 | 0.082 | 0.081 | 0.079 | 0.077 | 0.076 | 0.075 | 0.073 | 0.072 | 0.07
| 21.5 | 0.088 | 0.086 | 0.084 | 0.082 | 0.08 | 0.078 | 0.077 | 0.075 | 0.074 | 0.072 | 0.071 | 0.069 | 0.068 | 0.067 | 0.065 | 0.065 | 0.063
| 22 | 0.079 | 0.077 | 0.076 | 0.074 | 0.072 | 0.07 | 0.069 | 0.068 | 0.066 | 0.065 | 0.064 | 0.062 | 0.061 | 0.06 | 0.059 | 0.058 | 0.057
| 22.5 | 0.071 | 0.069 | 0.068 | 0.066 | 0.064 | 0.063 | 0.062 | 0.061 | 0.059 | 0.058 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053 | 0.052 | 0.051
| 23 | 0.064 | 0.062 | 0.061 | 0.06 | 0.058 | 0.057 | 0.056 | 0.055 | 0.054 | 0.052 | 0.051 | 0.05 | 0.049 | 0.049 | 0.048 | 0.047 | 0.046
| 23.5 | 0.057 | 0.056 | 0.055 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.042 | 0.041
| 24 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.04 | 0.039 | 0.038 | 0.038 | 0.037
| 24.5 | 0.047 | 0.045 | 0.045 | 0.043 | 0.042 | 0.041 | 0.041 | 0.04 | 0.039 | 0.038 | 0.037 | 0.037 | 0.036 | 0.035 | 0.035 | 0.034 | 0.033
| 25 | 0.042 | 0.041 | 0.04 | 0.039 | 0.038 | 0.038 | 0.037 | 0.036 | 0.035 | 0.035 | 0.034 | 0.033 | 0.032 | 0.032 | 0.031 | 0.031 | 0.03
| 25.5 | 0.038 | 0.037 | 0.036 | 0.035 | 0.034 | 0.034 | 0.033 | 0.032 | 0.032 | 0.031 | 0.03 | 0.03 | 0.029 | 0.029 | 0.028 | 0.028 | 0.027
| 26 | 0.035 | 0.034 | 0.033 | 0.032 | 0.031 | 0.031 | 0.03 | 0.03 | 0.029 | 0.028 | 0.028 | 0.027 | 0.027 | 0.026 | 0.026 | 0.025 | 0.025