## Sheet1
PROPERTIES
General
Name | Nordex N149/4.X Mode 3.b 4,2MW
Manufacturer | Nordex
Hub Height | 105 | 108 | 125 | 135 | 145 | 155 | 164
Power
Rated Power | 4200
Peak Power | 4200
Power Regulation Type | Pitch
Voltage | 660
Rotor
Rotor diameter | 149
Number of blades | 3
Rated RPM | 12.3
Rotor tilt | 6
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 26
Restart Wind Speed | 25.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 40
High Temperature Restart | 38
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | S
Values
Certification | IEC 3rd Edition
Vave | 7.5-9
Vref | 42
Design TI | 0.11

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 9 | 11 | 13 | 14 | 16 | 18 | 19 | 21 | 23 | 24 | 26 | 28 | 29 | 31 | 32 | 34 | 36
| 3.5 | 77 | 80 | 84 | 87 | 91 | 94 | 98 | 101 | 105 | 108 | 112 | 115 | 119 | 122 | 126 | 129 | 133
| 4 | 169 | 175 | 181 | 187 | 193 | 199 | 205 | 211 | 217 | 223 | 229 | 235 | 241 | 247 | 253 | 259 | 265
| 4.5 | 282 | 291 | 300 | 309 | 318 | 327 | 336 | 346 | 355 | 364 | 373 | 382 | 391 | 400 | 409 | 419 | 428
| 5 | 417 | 430 | 443 | 455 | 468 | 481 | 494 | 507 | 520 | 533 | 545 | 558 | 571 | 584 | 597 | 610 | 622
| 5.5 | 576 | 593 | 611 | 628 | 645 | 662 | 680 | 697 | 714 | 731 | 748 | 766 | 783 | 800 | 817 | 834 | 852
| 6 | 763 | 786 | 808 | 831 | 853 | 875 | 898 | 920 | 942 | 964 | 987 | 1009 | 1031 | 1054 | 1076 | 1098 | 1120
| 6.5 | 982 | 1010 | 1039 | 1067 | 1095 | 1123 | 1152 | 1180 | 1208 | 1236 | 1265 | 1293 | 1321 | 1349 | 1377 | 1405 | 1433
| 7 | 1235 | 1271 | 1306 | 1341 | 1376 | 1411 | 1446 | 1481 | 1516 | 1551 | 1586 | 1621 | 1656 | 1691 | 1726 | 1761 | 1796
| 7.5 | 1526 | 1569 | 1612 | 1655 | 1698 | 1741 | 1784 | 1827 | 1869 | 1912 | 1955 | 1998 | 2040 | 2083 | 2126 | 2168 | 2211
| 8 | 1856 | 1908 | 1960 | 2012 | 2064 | 2115 | 2167 | 2219 | 2270 | 2322 | 2373 | 2424 | 2475 | 2526 | 2577 | 2628 | 2678
| 8.5 | 2215 | 2280 | 2340 | 2402 | 2462 | 2522 | 2583 | 2644 | 2705 | 2766 | 2826 | 2894 | 2962 | 3029 | 3097 | 3159 | 3213
| 9 | 2583 | 2660 | 2730 | 2801 | 2872 | 2944 | 3017 | 3095 | 3173 | 3250 | 3323 | 3383 | 3443 | 3502 | 3562 | 3615 | 3659
| 9.5 | 2947 | 3038 | 3119 | 3204 | 3292 | 3379 | 3458 | 3525 | 3593 | 3659 | 3720 | 3765 | 3811 | 3856 | 3901 | 3940 | 3969
| 10 | 3307 | 3409 | 3504 | 3585 | 3660 | 3734 | 3799 | 3851 | 3901 | 3952 | 3996 | 4026 | 4054 | 4083 | 4111 | 4135 | 4152
| 10.5 | 3641 | 3724 | 3805 | 3870 | 3927 | 3983 | 4030 | 4062 | 4094 | 4127 | 4153 | 4166 | 4179 | 4191 | 4200 | 4200 | 4200
| 11 | 3892 | 3952 | 4014 | 4057 | 4093 | 4129 | 4156 | 4170 | 4184 | 4198 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 11.5 | 4061 | 4100 | 4138 | 4162 | 4177 | 4193 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 12 | 4158 | 4175 | 4193 | 4199 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 12.5 | 4196 | 4198 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 13 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 13.5 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 14 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 14.5 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 15 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 15.5 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 16 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 16.5 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 17 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 17.5 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 18 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 18.5 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 19 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 19.5 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 20 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 20.5 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 21 | 4185 | 4185 | 4185 | 4185 | 4185 | 4185 | 4185 | 4185 | 4185 | 4185 | 4185 | 4185 | 4185 | 4185 | 4185 | 4185 | 4185
| 21.5 | 4102 | 4102 | 4102 | 4102 | 4102 | 4102 | 4102 | 4102 | 4102 | 4102 | 4102 | 4102 | 4102 | 4102 | 4102 | 4102 | 4102
| 22 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951
| 22.5 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776
| 23 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600
| 23.5 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420
| 24 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245
| 24.5 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065
| 25 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885
| 25.5 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705
| 26 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431
| 3.5 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361
| 4 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736
| 4.5 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111
| 5 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556
| 5.5 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139
| 6 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931
| 6.5 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792
| 7 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54653 | 0.54653 | 0.54653 | 0.54653
| 7.5 | 0.54306 | 0.54306 | 0.54306 | 0.54306 | 0.54306 | 0.54306 | 0.54306 | 0.54306 | 0.54306 | 0.54306 | 0.54306 | 0.54306 | 0.54306 | 0.54306 | 0.54306 | 0.54306 | 0.54306
| 8 | 0.53056 | 0.53056 | 0.53056 | 0.53056 | 0.53056 | 0.53056 | 0.53056 | 0.53056 | 0.53056 | 0.53056 | 0.53056 | 0.52986 | 0.52847 | 0.52778 | 0.52708 | 0.52639 | 0.52431
| 8.5 | 0.51181 | 0.51181 | 0.51181 | 0.51181 | 0.51181 | 0.51181 | 0.51181 | 0.51111 | 0.50972 | 0.50833 | 0.50764 | 0.50486 | 0.50278 | 0.5 | 0.49792 | 0.49583 | 0.49306
| 9 | 0.48958 | 0.48958 | 0.48958 | 0.48958 | 0.4875 | 0.48611 | 0.48472 | 0.48264 | 0.48056 | 0.47778 | 0.47569 | 0.47292 | 0.46944 | 0.46597 | 0.46319 | 0.46042 | 0.45694
| 9.5 | 0.46458 | 0.46319 | 0.46181 | 0.46042 | 0.45764 | 0.45486 | 0.45278 | 0.45 | 0.44653 | 0.44375 | 0.44097 | 0.43681 | 0.43333 | 0.42986 | 0.42639 | 0.42292 | 0.41944
| 10 | 0.43472 | 0.43264 | 0.42986 | 0.42778 | 0.42431 | 0.42153 | 0.41875 | 0.41528 | 0.41111 | 0.40764 | 0.40417 | 0.40069 | 0.39653 | 0.39236 | 0.38889 | 0.38542 | 0.38125
| 10.5 | 0.40278 | 0.4 | 0.39722 | 0.39375 | 0.39028 | 0.38681 | 0.38333 | 0.37986 | 0.37569 | 0.37153 | 0.36806 | 0.36389 | 0.35972 | 0.35556 | 0.35139 | 0.34792 | 0.34375
| 11 | 0.37014 | 0.36667 | 0.36319 | 0.36042 | 0.35625 | 0.35208 | 0.34861 | 0.34444 | 0.34028 | 0.33611 | 0.33264 | 0.32778 | 0.32361 | 0.31944 | 0.31528 | 0.31111 | 0.30694
| 11.5 | 0.3375 | 0.33403 | 0.33056 | 0.32708 | 0.32222 | 0.31806 | 0.31458 | 0.31042 | 0.30556 | 0.30139 | 0.29792 | 0.29306 | 0.28889 | 0.28403 | 0.27986 | 0.27639 | 0.27222
| 12 | 0.30556 | 0.30208 | 0.29792 | 0.29444 | 0.28958 | 0.28542 | 0.28125 | 0.27708 | 0.27292 | 0.26806 | 0.26458 | 0.25972 | 0.25486 | 0.25069 | 0.24653 | 0.24306 | 0.23819
| 12.5 | 0.27569 | 0.27153 | 0.26736 | 0.26319 | 0.25903 | 0.25486 | 0.25069 | 0.24583 | 0.24167 | 0.2375 | 0.23333 | 0.22847 | 0.22431 | 0.21944 | 0.21528 | 0.21181 | 0.20764
| 13 | 0.24861 | 0.24444 | 0.24028 | 0.23611 | 0.23125 | 0.22708 | 0.22292 | 0.21875 | 0.21389 | 0.20972 | 0.20556 | 0.20139 | 0.19653 | 0.19167 | 0.18819 | 0.18403 | 0.17986
| 13.5 | 0.22431 | 0.22014 | 0.21528 | 0.21181 | 0.20694 | 0.20278 | 0.19861 | 0.19375 | 0.18958 | 0.18472 | 0.18125 | 0.17639 | 0.17222 | 0.16875 | 0.16528 | 0.16111 | 0.15833
| 14 | 0.20208 | 0.19792 | 0.19375 | 0.18958 | 0.18472 | 0.18056 | 0.17639 | 0.17222 | 0.16736 | 0.16319 | 0.15972 | 0.15625 | 0.15278 | 0.14931 | 0.14653 | 0.14375 | 0.14097
| 14.5 | 0.18264 | 0.17778 | 0.17361 | 0.16944 | 0.16528 | 0.16042 | 0.15694 | 0.15278 | 0.14931 | 0.14583 | 0.14236 | 0.13958 | 0.13611 | 0.13333 | 0.13056 | 0.12847 | 0.12569
| 15 | 0.16458 | 0.15972 | 0.15556 | 0.15139 | 0.14722 | 0.14375 | 0.14028 | 0.13681 | 0.13333 | 0.13056 | 0.12778 | 0.125 | 0.12222 | 0.12014 | 0.11806 | 0.11528 | 0.11319
| 15.5 | 0.14792 | 0.14375 | 0.14028 | 0.13611 | 0.13264 | 0.12917 | 0.12639 | 0.12361 | 0.12083 | 0.11806 | 0.11528 | 0.11319 | 0.11042 | 0.10833 | 0.10625 | 0.10417 | 0.10278
| 16 | 0.13403 | 0.12986 | 0.12639 | 0.12292 | 0.12014 | 0.11736 | 0.11458 | 0.11181 | 0.10903 | 0.10694 | 0.10486 | 0.10278 | 0.10069 | 0.098611 | 0.096528 | 0.095139 | 0.093056
| 16.5 | 0.12153 | 0.11806 | 0.11528 | 0.1125 | 0.10972 | 0.10694 | 0.10417 | 0.10208 | 0.1 | 0.097917 | 0.095833 | 0.09375 | 0.091667 | 0.090278 | 0.088194 | 0.086806 | 0.085417
| 17 | 0.11111 | 0.10833 | 0.10556 | 0.10278 | 0.10069 | 0.097917 | 0.095833 | 0.09375 | 0.091667 | 0.089583 | 0.088194 | 0.086111 | 0.084722 | 0.083333 | 0.08125 | 0.079861 | 0.078472
| 17.5 | 0.10278 | 0.1 | 0.097222 | 0.095139 | 0.093056 | 0.090972 | 0.088889 | 0.086806 | 0.084722 | 0.083333 | 0.08125 | 0.079861 | 0.078472 | 0.077083 | 0.075694 | 0.074306 | 0.072917
| 18 | 0.095833 | 0.093056 | 0.090972 | 0.088194 | 0.086111 | 0.084722 | 0.082639 | 0.080556 | 0.079167 | 0.077778 | 0.075694 | 0.074306 | 0.072917 | 0.071528 | 0.070139 | 0.069444 | 0.098
| 18.5 | 0.089583 | 0.086806 | 0.084722 | 0.082639 | 0.08125 | 0.079167 | 0.077083 | 0.075694 | 0.074306 | 0.072917 | 0.071528 | 0.070139 | 0.099 | 0.097 | 0.095 | 0.094 | 0.092
| 19 | 0.084028 | 0.081944 | 0.079861 | 0.078472 | 0.076389 | 0.074306 | 0.072917 | 0.071528 | 0.070139 | 0.099 | 0.097 | 0.095 | 0.093 | 0.092 | 0.09 | 0.088 | 0.087
| 19.5 | 0.079861 | 0.077778 | 0.075694 | 0.074306 | 0.072222 | 0.070833 | 0.069444 | 0.098 | 0.096 | 0.094 | 0.092 | 0.09 | 0.089 | 0.087 | 0.085 | 0.084 | 0.083
| 20 | 0.076389 | 0.074306 | 0.072222 | 0.070833 | 0.099 | 0.097 | 0.095 | 0.093 | 0.091 | 0.09 | 0.088 | 0.086 | 0.085 | 0.083 | 0.082 | 0.08 | 0.079
| 20.5 | 0.070833 | 0.099 | 0.096 | 0.094 | 0.091 | 0.09 | 0.088 | 0.086 | 0.084 | 0.083 | 0.081 | 0.079 | 0.078 | 0.077 | 0.076 | 0.074 | 0.073
| 21 | 0.092 | 0.09 | 0.087 | 0.086 | 0.083 | 0.081 | 0.08 | 0.078 | 0.076 | 0.076 | 0.074 | 0.072 | 0.071 | 0.07 | 0.069 | 0.067 | 0.066
| 21.5 | 0.083 | 0.08 | 0.078 | 0.077 | 0.074 | 0.073 | 0.071 | 0.07 | 0.068 | 0.068 | 0.066 | 0.065 | 0.064 | 0.062 | 0.062 | 0.06 | 0.059
| 22 | 0.074 | 0.072 | 0.07 | 0.069 | 0.067 | 0.066 | 0.064 | 0.063 | 0.062 | 0.061 | 0.06 | 0.058 | 0.058 | 0.056 | 0.056 | 0.054 | 0.053
| 22.5 | 0.067 | 0.065 | 0.063 | 0.062 | 0.06 | 0.059 | 0.058 | 0.056 | 0.055 | 0.055 | 0.053 | 0.052 | 0.052 | 0.05 | 0.05 | 0.048 | 0.048
| 23 | 0.06 | 0.058 | 0.057 | 0.056 | 0.054 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.045 | 0.044 | 0.043
| 23.5 | 0.054 | 0.052 | 0.051 | 0.05 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.044 | 0.043 | 0.042 | 0.041 | 0.041 | 0.04 | 0.039 | 0.039
| 24 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.04 | 0.039 | 0.038 | 0.037 | 0.037 | 0.036 | 0.035 | 0.035
| 24.5 | 0.044 | 0.043 | 0.041 | 0.041 | 0.039 | 0.039 | 0.038 | 0.037 | 0.036 | 0.036 | 0.035 | 0.034 | 0.034 | 0.033 | 0.033 | 0.032 | 0.031
| 25 | 0.04 | 0.039 | 0.038 | 0.037 | 0.036 | 0.035 | 0.034 | 0.034 | 0.033 | 0.032 | 0.032 | 0.031 | 0.031 | 0.03 | 0.03 | 0.029 | 0.029
| 25.5 | 0.036 | 0.035 | 0.034 | 0.033 | 0.032 | 0.031 | 0.031 | 0.03 | 0.029 | 0.029 | 0.028 | 0.028 | 0.027 | 0.027 | 0.026 | 0.026 | 0.026
| 26 | 0.032 | 0.032 | 0.031 | 0.03 | 0.029 | 0.029 | 0.028 | 0.027 | 0.027 | 0.027 | 0.026 | 0.025 | 0.025 | 0.024 | 0.024 | 0.024 | 0.023