## Sheet1
PROPERTIES
General
Name | Nordex N149/4.X Mode 5.a 4,2MW
Manufacturer | Nordex
Hub Height | 105 | 108 | 125 | 135 | 145 | 155 | 164
Power
Rated Power | 4200
Peak Power | 4200
Power Regulation Type | Pitch
Voltage | 660
Rotor
Rotor diameter | 149
Number of blades | 3
Rated RPM | 12.3
Rotor tilt | 6
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 26
Restart Wind Speed | 25.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 40
High Temperature Restart | 38
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | S
Values
Certification | IEC 3rd Edition
Vave | 7.5-9
Vref | 42
Design TI | 0.11

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 9 | 11 | 13 | 14 | 16 | 18 | 19 | 21 | 23 | 24 | 26 | 28 | 29 | 31 | 32 | 34 | 36
| 3.5 | 77 | 80 | 84 | 87 | 91 | 94 | 98 | 101 | 105 | 108 | 112 | 115 | 119 | 122 | 126 | 129 | 133
| 4 | 169 | 175 | 181 | 187 | 193 | 199 | 205 | 211 | 217 | 223 | 229 | 235 | 241 | 247 | 253 | 259 | 265
| 4.5 | 282 | 291 | 300 | 309 | 318 | 327 | 336 | 346 | 355 | 364 | 373 | 382 | 391 | 400 | 409 | 419 | 428
| 5 | 417 | 430 | 443 | 455 | 468 | 481 | 494 | 507 | 520 | 533 | 545 | 558 | 571 | 584 | 597 | 610 | 622
| 5.5 | 576 | 593 | 611 | 628 | 645 | 662 | 680 | 697 | 714 | 731 | 748 | 766 | 783 | 800 | 817 | 834 | 852
| 6 | 763 | 786 | 808 | 831 | 853 | 875 | 898 | 920 | 942 | 964 | 987 | 1009 | 1031 | 1054 | 1076 | 1098 | 1120
| 6.5 | 982 | 1010 | 1039 | 1067 | 1095 | 1124 | 1152 | 1180 | 1208 | 1236 | 1265 | 1293 | 1321 | 1349 | 1377 | 1405 | 1434
| 7 | 1235 | 1271 | 1306 | 1341 | 1376 | 1411 | 1446 | 1481 | 1516 | 1551 | 1586 | 1621 | 1656 | 1691 | 1726 | 1761 | 1796
| 7.5 | 1526 | 1570 | 1613 | 1656 | 1699 | 1741 | 1784 | 1827 | 1870 | 1913 | 1955 | 1998 | 2041 | 2083 | 2126 | 2169 | 2211
| 8 | 1850 | 1902 | 1953 | 2005 | 2058 | 2108 | 2160 | 2212 | 2263 | 2314 | 2365 | 2416 | 2467 | 2518 | 2569 | 2617 | 2665
| 8.5 | 2186 | 2247 | 2308 | 2368 | 2435 | 2489 | 2554 | 2613 | 2673 | 2733 | 2793 | 2852 | 2912 | 2978 | 3044 | 3097 | 3147
| 9 | 2520 | 2590 | 2659 | 2728 | 2806 | 2868 | 2945 | 3014 | 3083 | 3158 | 3233 | 3309 | 3384 | 3444 | 3500 | 3544 | 3584
| 9.5 | 2842 | 2922 | 2999 | 3077 | 3166 | 3240 | 3329 | 3414 | 3496 | 3563 | 3628 | 3694 | 3758 | 3803 | 3845 | 3875 | 3902
| 10 | 3146 | 3237 | 3325 | 3416 | 3514 | 3598 | 3672 | 3743 | 3815 | 3865 | 3914 | 3963 | 4011 | 4040 | 4067 | 4081 | 4095
| 10.5 | 3441 | 3542 | 3640 | 3718 | 3795 | 3869 | 3921 | 3974 | 4028 | 4060 | 4091 | 4122 | 4153 | 4166 | 4176 | 4182 | 4186
| 11 | 3715 | 3800 | 3881 | 3941 | 3997 | 4050 | 4084 | 4118 | 4151 | 4166 | 4180 | 4193 | 4200 | 4200 | 4200 | 4200 | 4200
| 11.5 | 3926 | 3988 | 4051 | 4088 | 4125 | 4157 | 4172 | 4187 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 12 | 4073 | 4113 | 4152 | 4169 | 4185 | 4199 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 12.5 | 4159 | 4177 | 4195 | 4197 | 4199 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 13 | 4193 | 4197 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 13.5 | 4199 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 14 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 14.5 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 15 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 15.5 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 16 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 16.5 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 17 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 17.5 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 18 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 18.5 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 19 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 19.5 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 20 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 20.5 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200 | 4200
| 21 | 4185 | 4185 | 4185 | 4185 | 4185 | 4185 | 4185 | 4185 | 4185 | 4185 | 4185 | 4185 | 4185 | 4185 | 4185 | 4185 | 4185
| 21.5 | 4102 | 4102 | 4102 | 4102 | 4102 | 4102 | 4102 | 4102 | 4102 | 4102 | 4102 | 4102 | 4102 | 4102 | 4102 | 4102 | 4102
| 22 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951 | 3951
| 22.5 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776 | 3776
| 23 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600
| 23.5 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420
| 24 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245
| 24.5 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065 | 3065
| 25 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885 | 2885
| 25.5 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705 | 2705
| 26 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529 | 2529

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431 | 0.57431
| 3.5 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361 | 0.57361
| 4 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736
| 4.5 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111
| 5 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556
| 5.5 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139 | 0.55139
| 6 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931
| 6.5 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792
| 7 | 0.54583 | 0.54583 | 0.54583 | 0.54583 | 0.54583 | 0.54583 | 0.54583 | 0.54583 | 0.54583 | 0.54583 | 0.54583 | 0.54583 | 0.54583 | 0.54583 | 0.54583 | 0.54583 | 0.54583
| 7.5 | 0.53472 | 0.53472 | 0.53472 | 0.53472 | 0.53472 | 0.53472 | 0.53472 | 0.53472 | 0.53472 | 0.53472 | 0.53472 | 0.53472 | 0.53472 | 0.53472 | 0.53472 | 0.53472 | 0.53403
| 8 | 0.51667 | 0.51667 | 0.51667 | 0.51667 | 0.51667 | 0.51667 | 0.51667 | 0.51667 | 0.51667 | 0.51667 | 0.51667 | 0.51667 | 0.51736 | 0.51667 | 0.51597 | 0.51528 | 0.51319
| 8.5 | 0.49444 | 0.49444 | 0.49444 | 0.49444 | 0.49444 | 0.49444 | 0.49444 | 0.49444 | 0.49444 | 0.49444 | 0.49306 | 0.49167 | 0.49097 | 0.49028 | 0.4875 | 0.48542 | 0.48264
| 9 | 0.46875 | 0.46875 | 0.46875 | 0.46875 | 0.46875 | 0.46875 | 0.46806 | 0.46667 | 0.46528 | 0.46458 | 0.4625 | 0.46042 | 0.45833 | 0.45625 | 0.45347 | 0.45069 | 0.44722
| 9.5 | 0.44167 | 0.44167 | 0.44167 | 0.44097 | 0.43958 | 0.43819 | 0.43681 | 0.43472 | 0.43264 | 0.43056 | 0.42778 | 0.425 | 0.42292 | 0.42014 | 0.41667 | 0.41319 | 0.40972
| 10 | 0.41319 | 0.4125 | 0.41111 | 0.40903 | 0.40694 | 0.40556 | 0.40278 | 0.4 | 0.39792 | 0.39514 | 0.39167 | 0.38889 | 0.38611 | 0.38333 | 0.37917 | 0.37569 | 0.37153
| 10.5 | 0.38264 | 0.38056 | 0.37847 | 0.37639 | 0.37361 | 0.37153 | 0.36875 | 0.36528 | 0.3625 | 0.35972 | 0.35625 | 0.35278 | 0.34931 | 0.34653 | 0.34236 | 0.33889 | 0.33472
| 11 | 0.35069 | 0.34861 | 0.34583 | 0.34306 | 0.34028 | 0.3375 | 0.33472 | 0.33125 | 0.32778 | 0.325 | 0.32083 | 0.31736 | 0.31389 | 0.31042 | 0.30625 | 0.30278 | 0.29861
| 11.5 | 0.31875 | 0.31597 | 0.31319 | 0.31042 | 0.30694 | 0.30417 | 0.30069 | 0.29722 | 0.29375 | 0.29028 | 0.28681 | 0.28264 | 0.27917 | 0.27569 | 0.27153 | 0.26806 | 0.26319
| 12 | 0.28889 | 0.28611 | 0.28264 | 0.27986 | 0.27639 | 0.27292 | 0.26944 | 0.26528 | 0.26181 | 0.25903 | 0.25486 | 0.25069 | 0.24722 | 0.24375 | 0.23958 | 0.23611 | 0.23125
| 12.5 | 0.26181 | 0.25833 | 0.25556 | 0.25208 | 0.24861 | 0.24514 | 0.24167 | 0.2375 | 0.23403 | 0.23056 | 0.22639 | 0.22292 | 0.21875 | 0.21528 | 0.21111 | 0.20764 | 0.20347
| 13 | 0.2375 | 0.23403 | 0.23056 | 0.22708 | 0.22361 | 0.22014 | 0.21667 | 0.2125 | 0.20903 | 0.20556 | 0.20139 | 0.19722 | 0.19375 | 0.19028 | 0.18611 | 0.18194 | 0.17847
| 13.5 | 0.21528 | 0.21181 | 0.20833 | 0.20486 | 0.20139 | 0.19792 | 0.19375 | 0.19028 | 0.18681 | 0.18264 | 0.17917 | 0.175 | 0.17153 | 0.16806 | 0.16389 | 0.16042 | 0.15694
| 14 | 0.19583 | 0.19236 | 0.18819 | 0.18472 | 0.18125 | 0.17778 | 0.17361 | 0.17014 | 0.16597 | 0.1625 | 0.15903 | 0.15486 | 0.15208 | 0.14861 | 0.14514 | 0.14236 | 0.13958
| 14.5 | 0.17778 | 0.17431 | 0.17014 | 0.16667 | 0.16319 | 0.15972 | 0.15556 | 0.15208 | 0.14861 | 0.14514 | 0.14167 | 0.13819 | 0.13542 | 0.13264 | 0.12986 | 0.12708 | 0.125
| 15 | 0.16111 | 0.15764 | 0.15417 | 0.15069 | 0.14653 | 0.14306 | 0.13958 | 0.13611 | 0.13264 | 0.12986 | 0.12708 | 0.12431 | 0.12153 | 0.11944 | 0.11667 | 0.11458 | 0.1125
| 15.5 | 0.14653 | 0.14306 | 0.13958 | 0.13542 | 0.13194 | 0.12847 | 0.12569 | 0.12292 | 0.12014 | 0.11736 | 0.11458 | 0.1125 | 0.10972 | 0.10764 | 0.10556 | 0.10347 | 0.10208
| 16 | 0.13333 | 0.12917 | 0.12569 | 0.12292 | 0.11944 | 0.11667 | 0.11389 | 0.11111 | 0.10833 | 0.10625 | 0.10417 | 0.10208 | 0.1 | 0.097917 | 0.095833 | 0.094444 | 0.092361
| 16.5 | 0.12083 | 0.11806 | 0.11458 | 0.11181 | 0.10903 | 0.10625 | 0.10347 | 0.10139 | 0.099306 | 0.097222 | 0.095139 | 0.093056 | 0.090972 | 0.089583 | 0.0875 | 0.086111 | 0.084722
| 17 | 0.11111 | 0.10764 | 0.10486 | 0.10278 | 0.1 | 0.097222 | 0.095139 | 0.093056 | 0.090972 | 0.088889 | 0.0875 | 0.085417 | 0.084028 | 0.082639 | 0.080556 | 0.079167 | 0.077778
| 17.5 | 0.10208 | 0.099306 | 0.097222 | 0.094444 | 0.092361 | 0.090278 | 0.088194 | 0.086111 | 0.084028 | 0.082639 | 0.080556 | 0.079167 | 0.077778 | 0.076389 | 0.075 | 0.073611 | 0.072222
| 18 | 0.095139 | 0.092361 | 0.090278 | 0.088194 | 0.086111 | 0.084028 | 0.081944 | 0.080556 | 0.078472 | 0.077083 | 0.075694 | 0.073611 | 0.072222 | 0.070833 | 0.070139 | 0.099 | 0.097
| 18.5 | 0.088889 | 0.086806 | 0.084722 | 0.082639 | 0.080556 | 0.078472 | 0.077083 | 0.075 | 0.073611 | 0.072222 | 0.070833 | 0.069444 | 0.098 | 0.096 | 0.094 | 0.093 | 0.091
| 19 | 0.084028 | 0.081944 | 0.079861 | 0.077778 | 0.075694 | 0.074306 | 0.072222 | 0.070833 | 0.069444 | 0.098 | 0.096 | 0.094 | 0.092 | 0.091 | 0.089 | 0.088 | 0.086
| 19.5 | 0.079167 | 0.077083 | 0.075694 | 0.073611 | 0.072222 | 0.070139 | 0.099 | 0.097 | 0.095 | 0.093 | 0.091 | 0.089 | 0.088 | 0.086 | 0.085 | 0.083 | 0.082
| 20 | 0.075694 | 0.073611 | 0.072222 | 0.070139 | 0.099 | 0.097 | 0.095 | 0.093 | 0.091 | 0.089 | 0.087 | 0.085 | 0.084 | 0.082 | 0.081 | 0.08 | 0.078
| 20.5 | 0.070139 | 0.098 | 0.096 | 0.093 | 0.091 | 0.09 | 0.088 | 0.086 | 0.084 | 0.082 | 0.08 | 0.078 | 0.078 | 0.076 | 0.075 | 0.074 | 0.072
| 21 | 0.091 | 0.089 | 0.087 | 0.085 | 0.083 | 0.081 | 0.08 | 0.078 | 0.076 | 0.075 | 0.073 | 0.071 | 0.07 | 0.069 | 0.068 | 0.067 | 0.065
| 21.5 | 0.082 | 0.08 | 0.078 | 0.076 | 0.074 | 0.073 | 0.071 | 0.07 | 0.068 | 0.067 | 0.065 | 0.064 | 0.063 | 0.062 | 0.061 | 0.06 | 0.059
| 22 | 0.074 | 0.072 | 0.07 | 0.068 | 0.067 | 0.066 | 0.064 | 0.063 | 0.062 | 0.06 | 0.059 | 0.058 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053
| 22.5 | 0.066 | 0.064 | 0.063 | 0.061 | 0.06 | 0.059 | 0.058 | 0.056 | 0.055 | 0.054 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047
| 23 | 0.06 | 0.058 | 0.057 | 0.055 | 0.054 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.046 | 0.046 | 0.045 | 0.044 | 0.044 | 0.043
| 23.5 | 0.053 | 0.052 | 0.051 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.041 | 0.04 | 0.04 | 0.039 | 0.038
| 24 | 0.048 | 0.047 | 0.046 | 0.044 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.038 | 0.037 | 0.037 | 0.036 | 0.036 | 0.035 | 0.034
| 24.5 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.038 | 0.037 | 0.036 | 0.035 | 0.035 | 0.034 | 0.033 | 0.033 | 0.032 | 0.032 | 0.031
| 25 | 0.039 | 0.038 | 0.038 | 0.036 | 0.036 | 0.035 | 0.034 | 0.034 | 0.033 | 0.032 | 0.031 | 0.031 | 0.03 | 0.03 | 0.029 | 0.029 | 0.028
| 25.5 | 0.035 | 0.034 | 0.034 | 0.033 | 0.032 | 0.031 | 0.031 | 0.03 | 0.029 | 0.029 | 0.028 | 0.027 | 0.027 | 0.026 | 0.026 | 0.026 | 0.025
| 26 | 0.032 | 0.031 | 0.031 | 0.03 | 0.029 | 0.029 | 0.028 | 0.027 | 0.027 | 0.026 | 0.026 | 0.025 | 0.025 | 0.024 | 0.024 | 0.024 | 0.023