## Sheet1
PROPERTIES
General
Name | Nordex N149/5.X 3,92MW
Manufacturer | Nordex
Hub Height | 105 | 120 | 125 | 145 | 155 | 164
Power
Rated Power | 3920
Peak Power | 3920
Power Regulation Type | Pitch
Voltage | 750
Rotor
Rotor diameter | 149
Number of blades | 3
Rated RPM | 20.5
Rotor tilt | 6
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 26
Restart Wind Speed | 25.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 50
High Temperature Restart | 40
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | S
Values
Certification | IEC 3rd Edition
Vave | 7.5-9.5
Vref | 42
Design TI | 0.11

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 18 | 20 | 23 | 24 | 26 | 29 | 31 | 33 | 34
| 3.5 | 95 | 98 | 102 | 105 | 109 | 113 | 116 | 120 | 123
| 4 | 203 | 209 | 215 | 221 | 227 | 233 | 239 | 246 | 252
| 4.5 | 337 | 346 | 355 | 364 | 374 | 383 | 392 | 401 | 410
| 5 | 498 | 510 | 523 | 536 | 549 | 561 | 574 | 587 | 600
| 5.5 | 688 | 705 | 722 | 739 | 756 | 773 | 790 | 807 | 824
| 6 | 911 | 933 | 955 | 977 | 999 | 1021 | 1043 | 1065 | 1087
| 6.5 | 1149 | 1176 | 1204 | 1231 | 1259 | 1286 | 1313 | 1341 | 1368
| 7 | 1385 | 1417 | 1450 | 1483 | 1515 | 1548 | 1581 | 1613 | 1646
| 7.5 | 1607 | 1645 | 1683 | 1720 | 1758 | 1796 | 1833 | 1871 | 1908
| 8 | 1814 | 1857 | 1899 | 1941 | 1984 | 2026 | 2068 | 2111 | 2153
| 8.5 | 2011 | 2057 | 2104 | 2151 | 2197 | 2244 | 2291 | 2337 | 2384
| 9 | 2200 | 2251 | 2302 | 2352 | 2403 | 2454 | 2505 | 2556 | 2607
| 9.5 | 2384 | 2439 | 2494 | 2549 | 2604 | 2658 | 2713 | 2768 | 2823
| 10 | 2563 | 2622 | 2681 | 2740 | 2799 | 2858 | 2917 | 2976 | 3035
| 10.5 | 2740 | 2803 | 2866 | 2929 | 2991 | 3054 | 3117 | 3180 | 3243
| 11 | 2913 | 2980 | 3047 | 3114 | 3180 | 3247 | 3315 | 3377 | 3438
| 11.5 | 3085 | 3155 | 3226 | 3297 | 3368 | 3430 | 3492 | 3546 | 3596
| 12 | 3254 | 3328 | 3402 | 3466 | 3530 | 3582 | 3633 | 3677 | 3717
| 12.5 | 3421 | 3487 | 3552 | 3605 | 3658 | 3700 | 3741 | 3775 | 3806
| 13 | 3561 | 3616 | 3670 | 3714 | 3757 | 3789 | 3821 | 3846 | 3867
| 13.5 | 3674 | 3719 | 3763 | 3796 | 3830 | 3853 | 3875 | 3891 | 3904
| 14 | 3762 | 3797 | 3831 | 3856 | 3880 | 3894 | 3908 | 3915 | 3918
| 14.5 | 3829 | 3855 | 3880 | 3895 | 3910 | 3915 | 3919 | 3920 | 3920
| 15 | 3876 | 3893 | 3909 | 3915 | 3920 | 3920 | 3920 | 3920 | 3920
| 15.5 | 3906 | 3913 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920
| 16 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920
| 16.5 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920
| 17 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920
| 17.5 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920
| 18 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920
| 18.5 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920
| 19 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920
| 19.5 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920
| 20 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920
| 20.5 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920
| 21 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920
| 21.5 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920
| 22 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920
| 22.5 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920
| 23 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920
| 23.5 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920
| 24 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920
| 24.5 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920
| 25 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920
| 25.5 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920
| 26 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920 | 3920

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986
| 3.5 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292
| 4 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597
| 4.5 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972
| 5 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417
| 5.5 | 0.54514 | 0.54514 | 0.54514 | 0.54514 | 0.54514 | 0.54514 | 0.54514 | 0.54514 | 0.54514
| 6 | 0.52222 | 0.52222 | 0.52222 | 0.52222 | 0.52222 | 0.52222 | 0.52222 | 0.52222 | 0.52222
| 6.5 | 0.49097 | 0.49097 | 0.49097 | 0.49097 | 0.49097 | 0.49097 | 0.49097 | 0.49097 | 0.49097
| 7 | 0.45625 | 0.45625 | 0.45625 | 0.45625 | 0.45625 | 0.45625 | 0.45625 | 0.45625 | 0.45625
| 7.5 | 0.41944 | 0.41944 | 0.41944 | 0.41944 | 0.41944 | 0.41944 | 0.41944 | 0.41944 | 0.41944
| 8 | 0.38264 | 0.38264 | 0.38264 | 0.38264 | 0.38264 | 0.38264 | 0.38264 | 0.38264 | 0.38264
| 8.5 | 0.34583 | 0.34583 | 0.34583 | 0.34583 | 0.34583 | 0.34583 | 0.34583 | 0.34583 | 0.34583
| 9 | 0.31042 | 0.31042 | 0.31042 | 0.31042 | 0.31042 | 0.31042 | 0.31042 | 0.31042 | 0.31042
| 9.5 | 0.28056 | 0.28056 | 0.28056 | 0.28056 | 0.28056 | 0.28056 | 0.28056 | 0.28056 | 0.28056
| 10 | 0.25486 | 0.25486 | 0.25486 | 0.25486 | 0.25486 | 0.25486 | 0.25486 | 0.25486 | 0.25417
| 10.5 | 0.23194 | 0.23194 | 0.23194 | 0.23194 | 0.23194 | 0.23194 | 0.23194 | 0.23194 | 0.23125
| 11 | 0.2125 | 0.2125 | 0.2125 | 0.2125 | 0.2125 | 0.21181 | 0.21111 | 0.21111 | 0.21042
| 11.5 | 0.19583 | 0.19514 | 0.19514 | 0.19444 | 0.19375 | 0.19375 | 0.19306 | 0.19167 | 0.19097
| 12 | 0.17986 | 0.17917 | 0.17917 | 0.17847 | 0.17778 | 0.17708 | 0.17569 | 0.175 | 0.17361
| 12.5 | 0.16597 | 0.16528 | 0.16458 | 0.16319 | 0.1625 | 0.16181 | 0.16042 | 0.15972 | 0.15833
| 13 | 0.15278 | 0.15208 | 0.15069 | 0.15 | 0.14931 | 0.14792 | 0.14653 | 0.14583 | 0.14444
| 13.5 | 0.14097 | 0.13958 | 0.13889 | 0.1375 | 0.13681 | 0.13542 | 0.13403 | 0.13333 | 0.13194
| 14 | 0.12986 | 0.12847 | 0.12778 | 0.12639 | 0.12569 | 0.12431 | 0.12292 | 0.12153 | 0.12014
| 14.5 | 0.12014 | 0.11875 | 0.11736 | 0.11667 | 0.11528 | 0.11389 | 0.1125 | 0.11111 | 0.10972
| 15 | 0.11042 | 0.10972 | 0.10833 | 0.10694 | 0.10625 | 0.10486 | 0.10347 | 0.10208 | 0.10069
| 15.5 | 0.10208 | 0.10139 | 0.1 | 0.098611 | 0.097222 | 0.095833 | 0.094444 | 0.09375 | 0.092361
| 16 | 0.094444 | 0.09375 | 0.092361 | 0.090972 | 0.089583 | 0.088194 | 0.086806 | 0.085417 | 0.084028
| 16.5 | 0.0875 | 0.086111 | 0.085417 | 0.084028 | 0.082639 | 0.08125 | 0.079861 | 0.078472 | 0.077083
| 17 | 0.08125 | 0.079861 | 0.078472 | 0.077083 | 0.075694 | 0.075 | 0.073611 | 0.072222 | 0.070833
| 17.5 | 0.075 | 0.074306 | 0.072917 | 0.071528 | 0.070139 | 0.099 | 0.097 | 0.095 | 0.093
| 18 | 0.070139 | 0.099 | 0.097 | 0.095 | 0.093 | 0.091 | 0.089 | 0.088 | 0.086
| 18.5 | 0.094 | 0.092 | 0.09 | 0.088 | 0.086 | 0.085 | 0.083 | 0.081 | 0.08
| 19 | 0.087 | 0.085 | 0.084 | 0.082 | 0.08 | 0.079 | 0.077 | 0.076 | 0.075
| 19.5 | 0.082 | 0.08 | 0.078 | 0.077 | 0.075 | 0.074 | 0.072 | 0.071 | 0.07
| 20 | 0.077 | 0.075 | 0.074 | 0.072 | 0.071 | 0.07 | 0.068 | 0.067 | 0.066
| 20.5 | 0.073 | 0.071 | 0.07 | 0.068 | 0.067 | 0.066 | 0.065 | 0.063 | 0.062
| 21 | 0.069 | 0.068 | 0.066 | 0.065 | 0.064 | 0.063 | 0.061 | 0.06 | 0.059
| 21.5 | 0.066 | 0.065 | 0.063 | 0.062 | 0.061 | 0.06 | 0.059 | 0.058 | 0.057
| 22 | 0.063 | 0.062 | 0.061 | 0.06 | 0.059 | 0.057 | 0.056 | 0.055 | 0.054
| 22.5 | 0.058 | 0.057 | 0.057 | 0.056 | 0.055 | 0.053 | 0.052 | 0.051 | 0.05
| 23 | 0.054 | 0.053 | 0.052 | 0.051 | 0.051 | 0.049 | 0.048 | 0.047 | 0.046
| 23.5 | 0.05 | 0.049 | 0.048 | 0.047 | 0.047 | 0.045 | 0.044 | 0.043 | 0.043
| 24 | 0.046 | 0.045 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.04
| 24.5 | 0.043 | 0.042 | 0.041 | 0.041 | 0.04 | 0.038 | 0.038 | 0.037 | 0.036
| 25 | 0.04 | 0.039 | 0.038 | 0.038 | 0.037 | 0.036 | 0.035 | 0.034 | 0.034
| 25.5 | 0.036 | 0.036 | 0.035 | 0.035 | 0.034 | 0.033 | 0.032 | 0.032 | 0.031
| 26 | 0.034 | 0.033 | 0.033 | 0.032 | 0.032 | 0.031 | 0.03 | 0.03 | 0.029