## Sheet1
PROPERTIES
General
Name | Nordex N149/5.X 3,2MW
Manufacturer | Nordex
Hub Height | 105 | 125 | 145 | 155 | 164
Power
Rated Power | 3200
Peak Power | 3200
Power Regulation Type | Pitch
Voltage | 750
Rotor
Rotor diameter | 149
Number of blades | 3
Rated RPM | 20.5
Rotor tilt | 6
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 26
Restart Wind Speed | 25.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 50
High Temperature Restart | 40
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | S
Values
Certification | IEC 3rd Edition
Vave | 7.5-9.5
Vref | 42
Design TI | 0.11

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 18 | 20 | 23 | 24 | 26 | 29 | 31 | 33 | 34
| 3.5 | 95 | 98 | 102 | 105 | 109 | 113 | 116 | 120 | 123
| 4 | 203 | 209 | 215 | 221 | 227 | 233 | 239 | 246 | 252
| 4.5 | 337 | 346 | 355 | 364 | 374 | 383 | 392 | 401 | 410
| 5 | 498 | 510 | 523 | 536 | 549 | 561 | 574 | 587 | 600
| 5.5 | 688 | 705 | 722 | 739 | 756 | 773 | 790 | 807 | 824
| 6 | 894 | 916 | 938 | 959 | 981 | 1003 | 1024 | 1046 | 1068
| 6.5 | 1100 | 1126 | 1152 | 1179 | 1205 | 1231 | 1257 | 1284 | 1310
| 7 | 1293 | 1324 | 1355 | 1385 | 1416 | 1447 | 1477 | 1508 | 1538
| 7.5 | 1473 | 1508 | 1542 | 1577 | 1612 | 1646 | 1681 | 1716 | 1750
| 8 | 1643 | 1681 | 1720 | 1758 | 1796 | 1835 | 1873 | 1912 | 1950
| 8.5 | 1806 | 1848 | 1890 | 1932 | 1975 | 2017 | 2059 | 2101 | 2143
| 9 | 1965 | 2011 | 2056 | 2102 | 2148 | 2193 | 2239 | 2285 | 2330
| 9.5 | 2120 | 2170 | 2219 | 2268 | 2317 | 2366 | 2415 | 2464 | 2513
| 10 | 2273 | 2326 | 2378 | 2431 | 2483 | 2535 | 2588 | 2641 | 2693
| 10.5 | 2423 | 2479 | 2535 | 2591 | 2647 | 2704 | 2756 | 2808 | 2856
| 11 | 2571 | 2631 | 2691 | 2749 | 2802 | 2856 | 2899 | 2941 | 2980
| 11.5 | 2720 | 2779 | 2834 | 2887 | 2930 | 2974 | 3009 | 3042 | 3073
| 12 | 2854 | 2905 | 2951 | 2994 | 3029 | 3064 | 3090 | 3115 | 3137
| 12.5 | 2962 | 3004 | 3041 | 3075 | 3102 | 3129 | 3147 | 3164 | 3178
| 13 | 3047 | 3080 | 3108 | 3134 | 3153 | 3171 | 3182 | 3191 | 3198
| 13.5 | 3111 | 3136 | 3156 | 3173 | 3184 | 3195 | 3198 | 3199 | 3200
| 14 | 3156 | 3173 | 3185 | 3195 | 3198 | 3200 | 3200 | 3200 | 3200
| 14.5 | 3185 | 3194 | 3198 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 15 | 3198 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 15.5 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 16 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 16.5 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 17 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 17.5 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 18 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 18.5 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 19 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 19.5 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 20 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 20.5 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 21 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 21.5 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 22 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 22.5 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 23 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 23.5 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 24 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 24.5 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 25 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 25.5 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 26 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986
| 3.5 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292
| 4 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597
| 4.5 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972
| 5 | 0.55278 | 0.55278 | 0.55278 | 0.55278 | 0.55278 | 0.55278 | 0.55278 | 0.55278 | 0.55278
| 5.5 | 0.52917 | 0.52917 | 0.52917 | 0.52917 | 0.52917 | 0.52917 | 0.52917 | 0.52917 | 0.52917
| 6 | 0.49653 | 0.49653 | 0.49653 | 0.49653 | 0.49653 | 0.49653 | 0.49653 | 0.49653 | 0.49653
| 6.5 | 0.45833 | 0.45833 | 0.45833 | 0.45833 | 0.45833 | 0.45833 | 0.45833 | 0.45833 | 0.45833
| 7 | 0.41875 | 0.41875 | 0.41875 | 0.41875 | 0.41875 | 0.41875 | 0.41875 | 0.41875 | 0.41875
| 7.5 | 0.37917 | 0.37917 | 0.37917 | 0.37917 | 0.37917 | 0.37917 | 0.37917 | 0.37917 | 0.37917
| 8 | 0.33958 | 0.33958 | 0.33958 | 0.33958 | 0.33958 | 0.33958 | 0.33958 | 0.33958 | 0.33958
| 8.5 | 0.30278 | 0.30278 | 0.30278 | 0.30278 | 0.30278 | 0.30278 | 0.30278 | 0.30278 | 0.30278
| 9 | 0.27153 | 0.27153 | 0.27153 | 0.27153 | 0.27153 | 0.27153 | 0.27153 | 0.27153 | 0.27153
| 9.5 | 0.24514 | 0.24514 | 0.24514 | 0.24514 | 0.24514 | 0.24514 | 0.24514 | 0.24514 | 0.24514
| 10 | 0.22222 | 0.22222 | 0.22222 | 0.22222 | 0.22222 | 0.22222 | 0.22222 | 0.22153 | 0.22153
| 10.5 | 0.20278 | 0.20278 | 0.20278 | 0.20278 | 0.20208 | 0.20208 | 0.20139 | 0.20069 | 0.2
| 11 | 0.18611 | 0.18542 | 0.18472 | 0.18472 | 0.18403 | 0.18333 | 0.18264 | 0.18194 | 0.18056
| 11.5 | 0.17014 | 0.16944 | 0.16875 | 0.16806 | 0.16736 | 0.16667 | 0.16597 | 0.16458 | 0.16389
| 12 | 0.15556 | 0.15486 | 0.15417 | 0.15347 | 0.15278 | 0.15139 | 0.15069 | 0.14931 | 0.14792
| 12.5 | 0.14306 | 0.14236 | 0.14097 | 0.14028 | 0.13889 | 0.13819 | 0.13681 | 0.13542 | 0.13472
| 13 | 0.13125 | 0.12986 | 0.12917 | 0.12778 | 0.12708 | 0.12569 | 0.12431 | 0.12361 | 0.12222
| 13.5 | 0.12014 | 0.11944 | 0.11806 | 0.11736 | 0.11597 | 0.11458 | 0.11319 | 0.1125 | 0.11111
| 14 | 0.11042 | 0.10972 | 0.10833 | 0.10694 | 0.10625 | 0.10486 | 0.10347 | 0.10208 | 0.10069
| 14.5 | 0.10208 | 0.10069 | 0.099306 | 0.097917 | 0.097222 | 0.095833 | 0.094444 | 0.093056 | 0.091667
| 15 | 0.09375 | 0.092361 | 0.090972 | 0.090278 | 0.088889 | 0.0875 | 0.086111 | 0.084722 | 0.083333
| 15.5 | 0.086111 | 0.085417 | 0.084028 | 0.082639 | 0.08125 | 0.079861 | 0.078472 | 0.077083 | 0.075694
| 16 | 0.079861 | 0.078472 | 0.077083 | 0.075694 | 0.074306 | 0.072917 | 0.071528 | 0.070139 | 0.069444
| 16.5 | 0.073611 | 0.072222 | 0.070833 | 0.069444 | 0.098 | 0.096 | 0.095 | 0.093 | 0.091
| 17 | 0.098 | 0.096 | 0.094 | 0.092 | 0.09 | 0.088 | 0.087 | 0.085 | 0.083
| 17.5 | 0.09 | 0.088 | 0.086 | 0.085 | 0.083 | 0.081 | 0.08 | 0.078 | 0.077
| 18 | 0.083 | 0.081 | 0.08 | 0.078 | 0.076 | 0.075 | 0.074 | 0.072 | 0.071
| 18.5 | 0.077 | 0.075 | 0.074 | 0.072 | 0.071 | 0.07 | 0.068 | 0.067 | 0.066
| 19 | 0.072 | 0.07 | 0.069 | 0.068 | 0.066 | 0.065 | 0.064 | 0.063 | 0.062
| 19.5 | 0.067 | 0.066 | 0.065 | 0.063 | 0.062 | 0.061 | 0.06 | 0.059 | 0.058
| 20 | 0.063 | 0.062 | 0.061 | 0.06 | 0.059 | 0.058 | 0.057 | 0.056 | 0.055
| 20.5 | 0.06 | 0.059 | 0.058 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053 | 0.052
| 21 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049
| 21.5 | 0.055 | 0.054 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047
| 22 | 0.053 | 0.051 | 0.05 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045
| 22.5 | 0.049 | 0.047 | 0.046 | 0.046 | 0.045 | 0.044 | 0.044 | 0.043 | 0.042
| 23 | 0.045 | 0.044 | 0.043 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039
| 23.5 | 0.042 | 0.04 | 0.04 | 0.04 | 0.039 | 0.038 | 0.037 | 0.036 | 0.036
| 24 | 0.039 | 0.037 | 0.037 | 0.037 | 0.036 | 0.035 | 0.034 | 0.034 | 0.033
| 24.5 | 0.036 | 0.034 | 0.034 | 0.034 | 0.033 | 0.032 | 0.032 | 0.031 | 0.03
| 25 | 0.033 | 0.032 | 0.031 | 0.031 | 0.031 | 0.03 | 0.029 | 0.029 | 0.028
| 25.5 | 0.031 | 0.029 | 0.029 | 0.029 | 0.028 | 0.028 | 0.027 | 0.027 | 0.026
| 26 | 0.029 | 0.027 | 0.027 | 0.027 | 0.026 | 0.026 | 0.025 | 0.025 | 0.024