## Sheet1
PROPERTIES
General
Name | Nordex N149/5.X 2,96MW
Manufacturer | Nordex
Hub Height | 105 | 125 | 145 | 155 | 164
Power
Rated Power | 2960
Peak Power | 2960
Power Regulation Type | Pitch
Voltage | 750
Rotor
Rotor diameter | 149
Number of blades | 3
Rated RPM | 20.5
Rotor tilt | 6
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 26
Restart Wind Speed | 25.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 50
High Temperature Restart | 40
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | S
Values
Certification | IEC 3rd Edition
Vave | 7.5-9.5
Vref | 42
Design TI | 0.11

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 18 | 20 | 23 | 24 | 26 | 29 | 31 | 33 | 34
| 3.5 | 95 | 98 | 102 | 105 | 109 | 113 | 116 | 120 | 123
| 4 | 203 | 209 | 215 | 221 | 227 | 233 | 239 | 246 | 252
| 4.5 | 337 | 346 | 355 | 364 | 374 | 383 | 392 | 401 | 410
| 5 | 498 | 510 | 523 | 536 | 549 | 561 | 574 | 587 | 600
| 5.5 | 686 | 703 | 720 | 737 | 754 | 771 | 787 | 804 | 821
| 6 | 883 | 905 | 926 | 948 | 969 | 991 | 1012 | 1033 | 1055
| 6.5 | 1076 | 1101 | 1127 | 1153 | 1179 | 1204 | 1230 | 1256 | 1282
| 7 | 1254 | 1284 | 1314 | 1344 | 1373 | 1403 | 1433 | 1463 | 1492
| 7.5 | 1420 | 1454 | 1487 | 1521 | 1554 | 1588 | 1621 | 1655 | 1688
| 8 | 1579 | 1616 | 1653 | 1690 | 1727 | 1764 | 1801 | 1838 | 1875
| 8.5 | 1732 | 1773 | 1813 | 1853 | 1894 | 1934 | 1975 | 2015 | 2056
| 9 | 1881 | 1925 | 1969 | 2013 | 2057 | 2100 | 2144 | 2188 | 2232
| 9.5 | 2028 | 2075 | 2122 | 2169 | 2216 | 2263 | 2310 | 2357 | 2404
| 10 | 2171 | 2222 | 2272 | 2322 | 2372 | 2423 | 2474 | 2522 | 2569
| 10.5 | 2313 | 2366 | 2420 | 2474 | 2526 | 2576 | 2626 | 2666 | 2704
| 11 | 2453 | 2510 | 2564 | 2615 | 2663 | 2703 | 2743 | 2775 | 2806
| 11.5 | 2588 | 2641 | 2687 | 2729 | 2768 | 2800 | 2832 | 2856 | 2878
| 12 | 2702 | 2745 | 2783 | 2816 | 2846 | 2870 | 2895 | 2911 | 2926
| 12.5 | 2790 | 2825 | 2855 | 2880 | 2902 | 2919 | 2935 | 2944 | 2952
| 13 | 2858 | 2884 | 2906 | 2924 | 2938 | 2948 | 2957 | 2959 | 2960
| 13.5 | 2906 | 2925 | 2939 | 2950 | 2957 | 2959 | 2960 | 2960 | 2960
| 14 | 2938 | 2950 | 2956 | 2959 | 2960 | 2960 | 2960 | 2960 | 2960
| 14.5 | 2955 | 2959 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960
| 15 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960
| 15.5 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960
| 16 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960
| 16.5 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960
| 17 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960
| 17.5 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960
| 18 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960
| 18.5 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960
| 19 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960
| 19.5 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960
| 20 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960
| 20.5 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960
| 21 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960
| 21.5 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960
| 22 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960
| 22.5 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960
| 23 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960
| 23.5 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960
| 24 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960
| 24.5 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960
| 25 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960
| 25.5 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960
| 26 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960 | 2960

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986
| 3.5 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292
| 4 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597
| 4.5 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972
| 5 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792 | 0.54792
| 5.5 | 0.52014 | 0.52014 | 0.52014 | 0.52014 | 0.52014 | 0.52014 | 0.52014 | 0.52014 | 0.52014
| 6 | 0.48403 | 0.48403 | 0.48403 | 0.48403 | 0.48403 | 0.48403 | 0.48403 | 0.48403 | 0.48403
| 6.5 | 0.44375 | 0.44375 | 0.44375 | 0.44375 | 0.44375 | 0.44375 | 0.44375 | 0.44375 | 0.44375
| 7 | 0.40278 | 0.40278 | 0.40278 | 0.40278 | 0.40278 | 0.40278 | 0.40278 | 0.40278 | 0.40278
| 7.5 | 0.36181 | 0.36181 | 0.36181 | 0.36181 | 0.36181 | 0.36181 | 0.36181 | 0.36181 | 0.36181
| 8 | 0.32292 | 0.32292 | 0.32292 | 0.32292 | 0.32292 | 0.32292 | 0.32292 | 0.32292 | 0.32292
| 8.5 | 0.2875 | 0.2875 | 0.2875 | 0.2875 | 0.2875 | 0.2875 | 0.2875 | 0.2875 | 0.2875
| 9 | 0.25833 | 0.25833 | 0.25833 | 0.25833 | 0.25833 | 0.25833 | 0.25833 | 0.25833 | 0.25833
| 9.5 | 0.23333 | 0.23333 | 0.23333 | 0.23333 | 0.23333 | 0.23333 | 0.23333 | 0.23333 | 0.23264
| 10 | 0.21181 | 0.21181 | 0.21181 | 0.21181 | 0.21111 | 0.21111 | 0.21042 | 0.21042 | 0.20972
| 10.5 | 0.19306 | 0.19306 | 0.19236 | 0.19236 | 0.19167 | 0.19097 | 0.19028 | 0.18958 | 0.18889
| 11 | 0.17639 | 0.17569 | 0.17569 | 0.175 | 0.17431 | 0.17361 | 0.17222 | 0.17153 | 0.17083
| 11.5 | 0.16111 | 0.16042 | 0.15972 | 0.15903 | 0.15833 | 0.15694 | 0.15625 | 0.15556 | 0.15417
| 12 | 0.14722 | 0.14653 | 0.14583 | 0.14514 | 0.14375 | 0.14306 | 0.14167 | 0.14028 | 0.13958
| 12.5 | 0.13472 | 0.13403 | 0.13333 | 0.13194 | 0.13125 | 0.12986 | 0.12847 | 0.12778 | 0.12639
| 13 | 0.12361 | 0.12292 | 0.12153 | 0.12014 | 0.11944 | 0.11806 | 0.11667 | 0.11597 | 0.11458
| 13.5 | 0.11319 | 0.1125 | 0.11111 | 0.10972 | 0.10903 | 0.10764 | 0.10625 | 0.10486 | 0.10347
| 14 | 0.10417 | 0.10278 | 0.10208 | 0.10069 | 0.099306 | 0.097917 | 0.096528 | 0.095139 | 0.09375
| 14.5 | 0.095833 | 0.094444 | 0.093056 | 0.091667 | 0.090972 | 0.089583 | 0.088194 | 0.086806 | 0.085417
| 15 | 0.088194 | 0.086806 | 0.085417 | 0.084028 | 0.082639 | 0.08125 | 0.079861 | 0.079167 | 0.077778
| 15.5 | 0.080556 | 0.079861 | 0.078472 | 0.077083 | 0.075694 | 0.074306 | 0.072917 | 0.071528 | 0.070139
| 16 | 0.074306 | 0.072917 | 0.071528 | 0.070833 | 0.069444 | 0.098 | 0.096 | 0.094 | 0.092
| 16.5 | 0.099 | 0.097 | 0.095 | 0.093 | 0.091 | 0.089 | 0.088 | 0.086 | 0.084
| 17 | 0.091 | 0.089 | 0.087 | 0.085 | 0.084 | 0.082 | 0.08 | 0.079 | 0.077
| 17.5 | 0.084 | 0.082 | 0.08 | 0.078 | 0.077 | 0.075 | 0.074 | 0.073 | 0.071
| 18 | 0.077 | 0.075 | 0.074 | 0.072 | 0.071 | 0.07 | 0.068 | 0.067 | 0.066
| 18.5 | 0.072 | 0.07 | 0.069 | 0.067 | 0.066 | 0.065 | 0.064 | 0.062 | 0.061
| 19 | 0.067 | 0.065 | 0.064 | 0.063 | 0.062 | 0.06 | 0.059 | 0.058 | 0.057
| 19.5 | 0.063 | 0.061 | 0.06 | 0.059 | 0.058 | 0.057 | 0.056 | 0.055 | 0.054
| 20 | 0.059 | 0.058 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053 | 0.052 | 0.051
| 20.5 | 0.056 | 0.055 | 0.054 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048
| 21 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.048 | 0.047 | 0.046
| 21.5 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.046 | 0.045 | 0.044
| 22 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.045 | 0.044 | 0.043 | 0.042
| 22.5 | 0.045 | 0.044 | 0.044 | 0.043 | 0.042 | 0.042 | 0.041 | 0.04 | 0.039
| 23 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.039 | 0.038 | 0.037 | 0.036
| 23.5 | 0.039 | 0.038 | 0.037 | 0.036 | 0.036 | 0.036 | 0.035 | 0.034 | 0.033
| 24 | 0.036 | 0.035 | 0.034 | 0.034 | 0.033 | 0.033 | 0.032 | 0.031 | 0.031
| 24.5 | 0.033 | 0.032 | 0.032 | 0.031 | 0.03 | 0.03 | 0.03 | 0.029 | 0.028
| 25 | 0.031 | 0.03 | 0.029 | 0.029 | 0.028 | 0.028 | 0.028 | 0.027 | 0.026
| 25.5 | 0.028 | 0.028 | 0.027 | 0.027 | 0.026 | 0.026 | 0.025 | 0.025 | 0.024
| 26 | 0.026 | 0.026 | 0.025 | 0.025 | 0.024 | 0.024 | 0.024 | 0.023 | 0.023