## Sheet1
PROPERTIES
General
Name | Nordex N149/5.X 5,5MW
Manufacturer | Nordex
Hub Height | 105 | 120 | 125 | 145 | 155 | 164
Power
Rated Power | 5500
Peak Power | 5500
Power Regulation Type | Pitch
Voltage | 750
Rotor
Rotor diameter | 149
Number of blades | 3
Rated RPM | 20.5
Rotor tilt | 6
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 26
Restart Wind Speed | 25.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 50
High Temperature Restart | 40
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | III
Turbine SubClass | S
Values
Certification | IEC 3rd Edition
Vave | 7.5-9.5
Vref | 42
Design TI | 0.11

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 2 | 4 | 5 | 8 | 10 | 12 | 13 | 16 | 18 | 20 | 23 | 24 | 26 | 29 | 31 | 33 | 34
| 3.5 | 66 | 70 | 73 | 77 | 80 | 84 | 87 | 91 | 95 | 98 | 102 | 105 | 109 | 113 | 116 | 120 | 123
| 4 | 155 | 161 | 167 | 173 | 179 | 185 | 191 | 197 | 203 | 209 | 215 | 221 | 227 | 233 | 239 | 246 | 252
| 4.5 | 264 | 273 | 283 | 292 | 301 | 310 | 319 | 328 | 337 | 346 | 355 | 364 | 374 | 383 | 392 | 401 | 410
| 5 | 396 | 409 | 421 | 434 | 447 | 460 | 472 | 485 | 498 | 510 | 523 | 536 | 549 | 561 | 574 | 587 | 600
| 5.5 | 552 | 569 | 586 | 603 | 620 | 637 | 654 | 671 | 688 | 705 | 722 | 739 | 756 | 773 | 790 | 807 | 824
| 6 | 736 | 758 | 780 | 802 | 825 | 847 | 869 | 891 | 913 | 935 | 957 | 979 | 1001 | 1023 | 1045 | 1068 | 1090
| 6.5 | 952 | 980 | 1008 | 1036 | 1065 | 1093 | 1121 | 1149 | 1177 | 1205 | 1233 | 1261 | 1289 | 1317 | 1345 | 1373 | 1401
| 7 | 1204 | 1239 | 1274 | 1309 | 1344 | 1379 | 1414 | 1449 | 1484 | 1519 | 1553 | 1588 | 1623 | 1658 | 1693 | 1728 | 1763
| 7.5 | 1493 | 1536 | 1579 | 1622 | 1665 | 1708 | 1751 | 1794 | 1836 | 1879 | 1922 | 1965 | 2008 | 2050 | 2093 | 2136 | 2178
| 8 | 1824 | 1875 | 1927 | 1979 | 2031 | 2083 | 2135 | 2187 | 2239 | 2290 | 2342 | 2394 | 2446 | 2497 | 2549 | 2601 | 2652
| 8.5 | 2187 | 2248 | 2310 | 2372 | 2434 | 2496 | 2557 | 2619 | 2681 | 2742 | 2804 | 2865 | 2927 | 2988 | 3050 | 3111 | 3173
| 9 | 2562 | 2635 | 2707 | 2779 | 2850 | 2922 | 2994 | 3066 | 3138 | 3210 | 3281 | 3353 | 3424 | 3496 | 3567 | 3639 | 3711
| 9.5 | 2936 | 3018 | 3101 | 3183 | 3265 | 3347 | 3429 | 3510 | 3592 | 3674 | 3755 | 3837 | 3919 | 4001 | 4083 | 4161 | 4240
| 10 | 3299 | 3391 | 3483 | 3575 | 3666 | 3758 | 3849 | 3941 | 4033 | 4125 | 4218 | 4305 | 4391 | 4477 | 4557 | 4623 | 4688
| 10.5 | 3644 | 3745 | 3847 | 3948 | 4048 | 4150 | 4252 | 4354 | 4448 | 4541 | 4634 | 4708 | 4780 | 4851 | 4917 | 4970 | 5022
| 11 | 3971 | 4081 | 4190 | 4301 | 4412 | 4517 | 4616 | 4715 | 4794 | 4871 | 4947 | 5008 | 5065 | 5122 | 5175 | 5214 | 5253
| 11.5 | 4283 | 4402 | 4521 | 4629 | 4733 | 4826 | 4908 | 4989 | 5054 | 5115 | 5177 | 5223 | 5266 | 5309 | 5347 | 5373 | 5399
| 12 | 4586 | 4699 | 4808 | 4900 | 4986 | 5062 | 5128 | 5194 | 5244 | 5290 | 5337 | 5369 | 5398 | 5427 | 5452 | 5464 | 5476
| 12.5 | 4846 | 4942 | 5033 | 5108 | 5178 | 5239 | 5290 | 5340 | 5375 | 5407 | 5440 | 5457 | 5472 | 5487 | 5498 | 5499 | 5499
| 13 | 5053 | 5132 | 5206 | 5266 | 5320 | 5365 | 5401 | 5436 | 5456 | 5474 | 5492 | 5496 | 5498 | 5500 | 5500 | 5500 | 5500
| 13.5 | 5213 | 5277 | 5334 | 5378 | 5417 | 5447 | 5468 | 5489 | 5494 | 5498 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 14 | 5334 | 5381 | 5423 | 5451 | 5475 | 5490 | 5496 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 14.5 | 5419 | 5451 | 5477 | 5490 | 5498 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 15 | 5473 | 5488 | 5499 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 15.5 | 5497 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 16 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 16.5 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 17 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 17.5 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 18 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 18.5 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 19 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 19.5 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 20 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 20.5 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 21 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 21.5 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 22 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 22.5 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 23 | 5469 | 5469 | 5469 | 5469 | 5469 | 5469 | 5469 | 5469 | 5469 | 5469 | 5469 | 5469 | 5469 | 5469 | 5469 | 5469 | 5469
| 23.5 | 5387 | 5387 | 5387 | 5387 | 5387 | 5387 | 5387 | 5387 | 5387 | 5387 | 5387 | 5387 | 5387 | 5387 | 5387 | 5387 | 5387
| 24 | 5278 | 5278 | 5278 | 5278 | 5278 | 5278 | 5278 | 5278 | 5278 | 5278 | 5278 | 5278 | 5278 | 5278 | 5278 | 5278 | 5278
| 24.5 | 5147 | 5147 | 5147 | 5147 | 5147 | 5147 | 5147 | 5147 | 5147 | 5147 | 5147 | 5147 | 5147 | 5147 | 5147 | 5147 | 5147
| 25 | 5039 | 5039 | 5039 | 5039 | 5039 | 5039 | 5039 | 5039 | 5039 | 5039 | 5039 | 5039 | 5039 | 5039 | 5039 | 5039 | 5039
| 25.5 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891
| 26 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986
| 3.5 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292
| 4 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597
| 4.5 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972
| 5 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417
| 5.5 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069
| 6 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861
| 6.5 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722
| 7 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722
| 7.5 | 0.54444 | 0.54444 | 0.54444 | 0.54444 | 0.54444 | 0.54444 | 0.54444 | 0.54444 | 0.54444 | 0.54444 | 0.54444 | 0.54444 | 0.54444 | 0.54444 | 0.54444 | 0.54444 | 0.54444
| 8 | 0.53264 | 0.53264 | 0.53264 | 0.53264 | 0.53264 | 0.53264 | 0.53264 | 0.53264 | 0.53264 | 0.53264 | 0.53264 | 0.53264 | 0.53264 | 0.53264 | 0.53264 | 0.53264 | 0.53264
| 8.5 | 0.51528 | 0.51528 | 0.51528 | 0.51528 | 0.51528 | 0.51528 | 0.51528 | 0.51528 | 0.51528 | 0.51528 | 0.51528 | 0.51528 | 0.51528 | 0.51528 | 0.51528 | 0.51528 | 0.51528
| 9 | 0.49375 | 0.49375 | 0.49375 | 0.49375 | 0.49375 | 0.49375 | 0.49375 | 0.49375 | 0.49375 | 0.49375 | 0.49375 | 0.49375 | 0.49375 | 0.49306 | 0.49306 | 0.49306 | 0.49167
| 9.5 | 0.46944 | 0.46944 | 0.46944 | 0.46944 | 0.46944 | 0.46944 | 0.46944 | 0.46944 | 0.46944 | 0.46944 | 0.46875 | 0.46875 | 0.46736 | 0.46597 | 0.46528 | 0.46389 | 0.46181
| 10 | 0.44444 | 0.44444 | 0.44444 | 0.44375 | 0.44444 | 0.44444 | 0.44375 | 0.44306 | 0.44306 | 0.44167 | 0.44028 | 0.43889 | 0.43681 | 0.43542 | 0.43333 | 0.43125 | 0.42847
| 10.5 | 0.41806 | 0.41806 | 0.41806 | 0.41806 | 0.41736 | 0.41667 | 0.41528 | 0.41389 | 0.4125 | 0.41111 | 0.40903 | 0.40694 | 0.40486 | 0.40208 | 0.4 | 0.39722 | 0.39444
| 11 | 0.39097 | 0.39097 | 0.39028 | 0.38958 | 0.38819 | 0.38681 | 0.38542 | 0.38333 | 0.38125 | 0.37917 | 0.37639 | 0.37431 | 0.37153 | 0.36875 | 0.36597 | 0.36389 | 0.36042
| 11.5 | 0.36389 | 0.36319 | 0.36181 | 0.36042 | 0.35833 | 0.35625 | 0.35417 | 0.35208 | 0.35 | 0.34722 | 0.34444 | 0.34167 | 0.33889 | 0.33611 | 0.33333 | 0.32986 | 0.32639
| 12 | 0.33542 | 0.33403 | 0.33264 | 0.33056 | 0.32847 | 0.32569 | 0.32361 | 0.32083 | 0.31875 | 0.31528 | 0.3125 | 0.30972 | 0.30625 | 0.30347 | 0.30069 | 0.29722 | 0.29375
| 12.5 | 0.30764 | 0.30625 | 0.30347 | 0.30139 | 0.29861 | 0.29653 | 0.29375 | 0.29097 | 0.28819 | 0.28472 | 0.28194 | 0.27917 | 0.27569 | 0.27222 | 0.26944 | 0.26597 | 0.2625
| 13 | 0.28194 | 0.27986 | 0.27778 | 0.275 | 0.27222 | 0.26944 | 0.26667 | 0.26389 | 0.26111 | 0.25764 | 0.25417 | 0.25139 | 0.24792 | 0.24444 | 0.24167 | 0.23819 | 0.23472
| 13.5 | 0.25903 | 0.25694 | 0.25417 | 0.25139 | 0.24861 | 0.24514 | 0.24236 | 0.23958 | 0.23611 | 0.23264 | 0.22986 | 0.22639 | 0.22292 | 0.21944 | 0.21667 | 0.21319 | 0.20972
| 14 | 0.2375 | 0.23542 | 0.23264 | 0.22986 | 0.22639 | 0.22361 | 0.22014 | 0.21736 | 0.21389 | 0.21042 | 0.20764 | 0.20417 | 0.20069 | 0.19722 | 0.19375 | 0.19097 | 0.18681
| 14.5 | 0.21875 | 0.21597 | 0.2125 | 0.20972 | 0.20694 | 0.20347 | 0.20069 | 0.19722 | 0.19375 | 0.19028 | 0.1875 | 0.18403 | 0.18056 | 0.17708 | 0.17361 | 0.17083 | 0.16667
| 15 | 0.20069 | 0.19792 | 0.19514 | 0.19167 | 0.18889 | 0.18542 | 0.18194 | 0.17917 | 0.17569 | 0.17222 | 0.16875 | 0.16597 | 0.1625 | 0.15903 | 0.15556 | 0.15208 | 0.14931
| 15.5 | 0.18472 | 0.18194 | 0.17847 | 0.17569 | 0.17222 | 0.16875 | 0.16597 | 0.1625 | 0.15903 | 0.15556 | 0.15278 | 0.14931 | 0.14583 | 0.14306 | 0.13958 | 0.13681 | 0.13403
| 16 | 0.16944 | 0.16667 | 0.16389 | 0.16042 | 0.15694 | 0.15417 | 0.15069 | 0.14722 | 0.14444 | 0.14097 | 0.1375 | 0.13472 | 0.13194 | 0.12917 | 0.12639 | 0.12361 | 0.12153
| 16.5 | 0.15625 | 0.15347 | 0.15 | 0.14653 | 0.14375 | 0.14028 | 0.13681 | 0.13403 | 0.13056 | 0.12778 | 0.125 | 0.12222 | 0.11944 | 0.11736 | 0.11458 | 0.1125 | 0.11042
| 17 | 0.14375 | 0.14097 | 0.1375 | 0.13403 | 0.13125 | 0.12778 | 0.125 | 0.12153 | 0.11875 | 0.11597 | 0.11389 | 0.11111 | 0.10903 | 0.10694 | 0.10486 | 0.10278 | 0.10069
| 17.5 | 0.13194 | 0.12917 | 0.12569 | 0.12292 | 0.11944 | 0.11667 | 0.11389 | 0.11111 | 0.10833 | 0.10625 | 0.10417 | 0.10208 | 0.1 | 0.097917 | 0.095833 | 0.09375 | 0.092361
| 18 | 0.12153 | 0.11875 | 0.11528 | 0.1125 | 0.10972 | 0.10694 | 0.10417 | 0.10208 | 0.1 | 0.097917 | 0.095833 | 0.09375 | 0.091667 | 0.090278 | 0.088194 | 0.086806 | 0.084722
| 18.5 | 0.1125 | 0.10972 | 0.10694 | 0.10417 | 0.10139 | 0.098611 | 0.096528 | 0.094444 | 0.092361 | 0.090278 | 0.088194 | 0.086806 | 0.084722 | 0.083333 | 0.081944 | 0.079861 | 0.078472
| 19 | 0.10417 | 0.10139 | 0.098611 | 0.096528 | 0.09375 | 0.091667 | 0.089583 | 0.0875 | 0.086111 | 0.084028 | 0.081944 | 0.080556 | 0.079167 | 0.077778 | 0.076389 | 0.075 | 0.073611
| 19.5 | 0.097222 | 0.094444 | 0.092361 | 0.090278 | 0.0875 | 0.085417 | 0.084028 | 0.081944 | 0.079861 | 0.078472 | 0.077083 | 0.075694 | 0.073611 | 0.072222 | 0.071528 | 0.070139 | 0.099
| 20 | 0.090972 | 0.088889 | 0.086806 | 0.084722 | 0.082639 | 0.080556 | 0.078472 | 0.077083 | 0.075694 | 0.073611 | 0.072222 | 0.070833 | 0.069444 | 0.098 | 0.096 | 0.095 | 0.093
| 20.5 | 0.086111 | 0.084028 | 0.081944 | 0.079861 | 0.077778 | 0.076389 | 0.074306 | 0.072917 | 0.071528 | 0.069444 | 0.098 | 0.096 | 0.095 | 0.093 | 0.091 | 0.09 | 0.088
| 21 | 0.081944 | 0.079861 | 0.077778 | 0.075694 | 0.073611 | 0.072222 | 0.070833 | 0.099 | 0.097 | 0.095 | 0.093 | 0.092 | 0.09 | 0.088 | 0.087 | 0.085 | 0.084
| 21.5 | 0.077778 | 0.075694 | 0.073611 | 0.072222 | 0.070139 | 0.099 | 0.097 | 0.095 | 0.093 | 0.091 | 0.089 | 0.088 | 0.086 | 0.084 | 0.083 | 0.081 | 0.08
| 22 | 0.074306 | 0.072222 | 0.070833 | 0.099 | 0.097 | 0.095 | 0.093 | 0.091 | 0.089 | 0.087 | 0.086 | 0.084 | 0.082 | 0.081 | 0.079 | 0.078 | 0.077
| 22.5 | 0.099 | 0.096 | 0.095 | 0.092 | 0.09 | 0.088 | 0.086 | 0.084 | 0.083 | 0.081 | 0.08 | 0.078 | 0.076 | 0.075 | 0.073 | 0.072 | 0.071
| 23 | 0.092 | 0.089 | 0.087 | 0.085 | 0.083 | 0.081 | 0.08 | 0.078 | 0.076 | 0.075 | 0.074 | 0.072 | 0.07 | 0.069 | 0.068 | 0.067 | 0.066
| 23.5 | 0.085 | 0.082 | 0.081 | 0.078 | 0.077 | 0.075 | 0.073 | 0.072 | 0.07 | 0.069 | 0.068 | 0.066 | 0.065 | 0.064 | 0.062 | 0.062 | 0.061
| 24 | 0.078 | 0.076 | 0.075 | 0.072 | 0.071 | 0.07 | 0.068 | 0.067 | 0.065 | 0.064 | 0.063 | 0.061 | 0.06 | 0.059 | 0.058 | 0.057 | 0.056
| 24.5 | 0.072 | 0.07 | 0.069 | 0.067 | 0.065 | 0.064 | 0.063 | 0.061 | 0.06 | 0.059 | 0.058 | 0.057 | 0.055 | 0.055 | 0.053 | 0.053 | 0.052
| 25 | 0.067 | 0.065 | 0.064 | 0.062 | 0.061 | 0.06 | 0.058 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053 | 0.051 | 0.051 | 0.05 | 0.049 | 0.048
| 25.5 | 0.062 | 0.06 | 0.059 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053 | 0.051 | 0.05 | 0.05 | 0.049 | 0.047 | 0.047 | 0.046 | 0.045 | 0.045
| 26 | 0.058 | 0.056 | 0.055 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.044 | 0.043 | 0.042 | 0.041