## Sheet1
PROPERTIES
General
Name | Nordex N149/5.X 5,3MW
Manufacturer | Nordex
Hub Height | 105 | 120 | 125 | 145 | 155 | 164
Power
Rated Power | 5300
Peak Power | 5300
Power Regulation Type | Pitch
Voltage | 750
Rotor
Rotor diameter | 149
Number of blades | 3
Rated RPM | 20.5
Rotor tilt | 6
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 26
Restart Wind Speed | 25.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 50
High Temperature Restart | 40
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | III
Turbine SubClass | S
Values
Certification | IEC 3rd Edition
Vave | 7.5-9.5
Vref | 42
Design TI | 0.11

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 2 | 4 | 5 | 8 | 10 | 12 | 13 | 16 | 18 | 20 | 23 | 24 | 26 | 29 | 31 | 33 | 34
| 3.5 | 66 | 70 | 73 | 77 | 80 | 84 | 87 | 91 | 95 | 98 | 102 | 105 | 109 | 113 | 116 | 120 | 123
| 4 | 155 | 161 | 167 | 173 | 179 | 185 | 191 | 197 | 203 | 209 | 215 | 221 | 227 | 233 | 239 | 246 | 252
| 4.5 | 264 | 273 | 283 | 292 | 301 | 310 | 319 | 328 | 337 | 346 | 355 | 364 | 374 | 383 | 392 | 401 | 410
| 5 | 396 | 409 | 421 | 434 | 447 | 460 | 472 | 485 | 498 | 510 | 523 | 536 | 549 | 561 | 574 | 587 | 600
| 5.5 | 552 | 569 | 586 | 603 | 620 | 637 | 654 | 671 | 688 | 705 | 722 | 739 | 756 | 773 | 790 | 807 | 824
| 6 | 736 | 758 | 780 | 802 | 824 | 847 | 869 | 891 | 913 | 935 | 957 | 979 | 1001 | 1023 | 1045 | 1068 | 1090
| 6.5 | 952 | 980 | 1008 | 1036 | 1065 | 1093 | 1121 | 1149 | 1177 | 1205 | 1233 | 1261 | 1289 | 1317 | 1345 | 1373 | 1401
| 7 | 1204 | 1239 | 1274 | 1309 | 1344 | 1379 | 1414 | 1449 | 1484 | 1518 | 1553 | 1588 | 1623 | 1658 | 1693 | 1728 | 1763
| 7.5 | 1493 | 1536 | 1579 | 1622 | 1665 | 1708 | 1751 | 1794 | 1837 | 1879 | 1922 | 1965 | 2008 | 2051 | 2093 | 2136 | 2179
| 8 | 1820 | 1872 | 1924 | 1976 | 2028 | 2079 | 2131 | 2183 | 2235 | 2286 | 2338 | 2390 | 2441 | 2493 | 2544 | 2596 | 2647
| 8.5 | 2167 | 2228 | 2289 | 2351 | 2412 | 2473 | 2534 | 2596 | 2657 | 2718 | 2779 | 2840 | 2901 | 2962 | 3023 | 3083 | 3144
| 9 | 2515 | 2586 | 2657 | 2728 | 2799 | 2869 | 2940 | 3010 | 3081 | 3151 | 3222 | 3292 | 3362 | 3433 | 3503 | 3573 | 3643
| 9.5 | 2856 | 2936 | 3016 | 3096 | 3176 | 3255 | 3335 | 3415 | 3495 | 3574 | 3653 | 3733 | 3813 | 3893 | 3973 | 4050 | 4127
| 10 | 3181 | 3270 | 3358 | 3447 | 3536 | 3624 | 3713 | 3801 | 3889 | 3978 | 4067 | 4156 | 4239 | 4322 | 4406 | 4477 | 4540
| 10.5 | 3488 | 3585 | 3682 | 3779 | 3876 | 3972 | 4069 | 4167 | 4264 | 4354 | 4443 | 4530 | 4599 | 4667 | 4736 | 4793 | 4844
| 11 | 3780 | 3885 | 3990 | 4094 | 4200 | 4305 | 4404 | 4499 | 4592 | 4665 | 4738 | 4810 | 4865 | 4920 | 4975 | 5019 | 5056
| 11.5 | 4062 | 4174 | 4287 | 4401 | 4502 | 4600 | 4686 | 4764 | 4841 | 4900 | 4959 | 5016 | 5057 | 5098 | 5139 | 5170 | 5195
| 12 | 4336 | 4456 | 4562 | 4665 | 4750 | 4832 | 4902 | 4965 | 5027 | 5072 | 5116 | 5159 | 5187 | 5215 | 5243 | 5260 | 5272
| 12.5 | 4591 | 4698 | 4787 | 4873 | 4942 | 5009 | 5064 | 5112 | 5159 | 5190 | 5221 | 5250 | 5264 | 5278 | 5293 | 5298 | 5299
| 13 | 4800 | 4889 | 4963 | 5033 | 5087 | 5138 | 5179 | 5213 | 5246 | 5263 | 5280 | 5295 | 5297 | 5299 | 5300 | 5300 | 5300
| 13.5 | 4965 | 5038 | 5096 | 5151 | 5190 | 5227 | 5253 | 5273 | 5292 | 5295 | 5298 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300
| 14 | 5092 | 5150 | 5192 | 5232 | 5257 | 5279 | 5292 | 5297 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300
| 14.5 | 5186 | 5228 | 5256 | 5281 | 5291 | 5299 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300
| 15 | 5249 | 5277 | 5290 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300
| 15.5 | 5286 | 5298 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300
| 16 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300
| 16.5 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300
| 17 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300
| 17.5 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300
| 18 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300
| 18.5 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300
| 19 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300
| 19.5 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300
| 20 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300
| 20.5 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300
| 21 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300
| 21.5 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300
| 22 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300
| 22.5 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300
| 23 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300 | 5300
| 23.5 | 5297 | 5297 | 5297 | 5297 | 5297 | 5297 | 5297 | 5297 | 5297 | 5297 | 5297 | 5297 | 5297 | 5297 | 5297 | 5297 | 5297
| 24 | 5251 | 5251 | 5251 | 5251 | 5251 | 5251 | 5251 | 5251 | 5251 | 5251 | 5251 | 5251 | 5251 | 5251 | 5251 | 5251 | 5251
| 24.5 | 5147 | 5147 | 5147 | 5147 | 5147 | 5147 | 5147 | 5147 | 5147 | 5147 | 5147 | 5147 | 5147 | 5147 | 5147 | 5147 | 5147
| 25 | 5039 | 5039 | 5039 | 5039 | 5039 | 5039 | 5039 | 5039 | 5039 | 5039 | 5039 | 5039 | 5039 | 5039 | 5039 | 5039 | 5039
| 25.5 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891
| 26 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986
| 3.5 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292
| 4 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597
| 4.5 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972
| 5 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417
| 5.5 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069
| 6 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861
| 6.5 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722
| 7 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54653
| 7.5 | 0.53819 | 0.53819 | 0.53819 | 0.53819 | 0.53819 | 0.53819 | 0.53819 | 0.53819 | 0.53819 | 0.53819 | 0.53819 | 0.53819 | 0.53819 | 0.53819 | 0.53819 | 0.53819 | 0.53819
| 8 | 0.52222 | 0.52222 | 0.52222 | 0.52222 | 0.52222 | 0.52222 | 0.52222 | 0.52222 | 0.52222 | 0.52222 | 0.52222 | 0.52222 | 0.52222 | 0.52222 | 0.52222 | 0.52222 | 0.52222
| 8.5 | 0.50069 | 0.50069 | 0.50069 | 0.50069 | 0.50069 | 0.50069 | 0.50069 | 0.50069 | 0.50069 | 0.50069 | 0.50069 | 0.50069 | 0.50069 | 0.50069 | 0.50069 | 0.50069 | 0.50069
| 9 | 0.47639 | 0.47639 | 0.47639 | 0.47639 | 0.47639 | 0.47639 | 0.47639 | 0.47639 | 0.47639 | 0.47639 | 0.47639 | 0.47639 | 0.47639 | 0.47639 | 0.47639 | 0.47639 | 0.47569
| 9.5 | 0.45069 | 0.45069 | 0.45069 | 0.45069 | 0.45069 | 0.45069 | 0.45 | 0.45069 | 0.45069 | 0.45069 | 0.45 | 0.45 | 0.44931 | 0.44792 | 0.44722 | 0.44583 | 0.44444
| 10 | 0.42292 | 0.42292 | 0.42292 | 0.42292 | 0.42292 | 0.42292 | 0.42292 | 0.42292 | 0.42222 | 0.42222 | 0.42083 | 0.41944 | 0.41875 | 0.41667 | 0.41458 | 0.41319 | 0.41111
| 10.5 | 0.39583 | 0.39583 | 0.39583 | 0.39583 | 0.39583 | 0.39514 | 0.39444 | 0.39375 | 0.39236 | 0.39097 | 0.38889 | 0.3875 | 0.38611 | 0.38333 | 0.38125 | 0.37917 | 0.37708
| 11 | 0.36806 | 0.36806 | 0.36806 | 0.36736 | 0.36667 | 0.36528 | 0.36389 | 0.3625 | 0.36111 | 0.35903 | 0.35694 | 0.35486 | 0.35278 | 0.35 | 0.34792 | 0.34514 | 0.34306
| 11.5 | 0.34097 | 0.34028 | 0.33958 | 0.33819 | 0.33681 | 0.33472 | 0.33333 | 0.33125 | 0.32917 | 0.32708 | 0.325 | 0.32222 | 0.32014 | 0.31736 | 0.31458 | 0.31181 | 0.30903
| 12 | 0.31319 | 0.3125 | 0.31111 | 0.30903 | 0.30764 | 0.30556 | 0.30347 | 0.30139 | 0.29861 | 0.29653 | 0.29375 | 0.29097 | 0.28889 | 0.28542 | 0.28264 | 0.27986 | 0.27708
| 12.5 | 0.28819 | 0.28611 | 0.28472 | 0.28264 | 0.28056 | 0.27847 | 0.27639 | 0.27361 | 0.27083 | 0.26875 | 0.26597 | 0.26319 | 0.26042 | 0.25694 | 0.25417 | 0.25139 | 0.24861
| 13 | 0.26458 | 0.2625 | 0.26042 | 0.25833 | 0.25625 | 0.25347 | 0.25139 | 0.24861 | 0.24583 | 0.24306 | 0.24028 | 0.2375 | 0.23472 | 0.23125 | 0.22847 | 0.22569 | 0.22222
| 13.5 | 0.24306 | 0.24097 | 0.23889 | 0.23611 | 0.23403 | 0.23125 | 0.22847 | 0.22569 | 0.22292 | 0.22014 | 0.21736 | 0.21458 | 0.21181 | 0.20833 | 0.20556 | 0.20208 | 0.19931
| 14 | 0.22361 | 0.22153 | 0.21875 | 0.21667 | 0.21389 | 0.21111 | 0.20833 | 0.20556 | 0.20278 | 0.2 | 0.19653 | 0.19375 | 0.19097 | 0.1875 | 0.18472 | 0.18194 | 0.17847
| 14.5 | 0.20625 | 0.20347 | 0.20069 | 0.19792 | 0.19583 | 0.19306 | 0.19028 | 0.18681 | 0.18403 | 0.18125 | 0.17778 | 0.175 | 0.17222 | 0.16875 | 0.16597 | 0.1625 | 0.15972
| 15 | 0.18958 | 0.18681 | 0.18472 | 0.18194 | 0.17917 | 0.17569 | 0.17292 | 0.17014 | 0.16736 | 0.16458 | 0.16111 | 0.15833 | 0.15556 | 0.15208 | 0.14861 | 0.14583 | 0.14306
| 15.5 | 0.175 | 0.17222 | 0.16944 | 0.16667 | 0.16389 | 0.16111 | 0.15764 | 0.15486 | 0.15208 | 0.14931 | 0.14583 | 0.14306 | 0.13958 | 0.13681 | 0.13403 | 0.13125 | 0.12847
| 16 | 0.16111 | 0.15833 | 0.15556 | 0.15278 | 0.15 | 0.14722 | 0.14375 | 0.14097 | 0.13819 | 0.13542 | 0.13194 | 0.12917 | 0.12639 | 0.12361 | 0.12083 | 0.11875 | 0.11667
| 16.5 | 0.14861 | 0.14583 | 0.14306 | 0.14028 | 0.1375 | 0.13403 | 0.13125 | 0.12847 | 0.125 | 0.12222 | 0.11944 | 0.11736 | 0.11458 | 0.1125 | 0.11042 | 0.10764 | 0.10625
| 17 | 0.13681 | 0.13403 | 0.13125 | 0.12847 | 0.12569 | 0.12222 | 0.11944 | 0.11667 | 0.11389 | 0.11181 | 0.10903 | 0.10694 | 0.10486 | 0.10278 | 0.10069 | 0.098611 | 0.096528
| 17.5 | 0.12639 | 0.12361 | 0.12083 | 0.11806 | 0.11458 | 0.11181 | 0.10903 | 0.10694 | 0.10417 | 0.10208 | 0.1 | 0.097917 | 0.095833 | 0.09375 | 0.092361 | 0.090278 | 0.088889
| 18 | 0.11667 | 0.11389 | 0.11111 | 0.10833 | 0.10556 | 0.10278 | 0.10069 | 0.097917 | 0.095833 | 0.09375 | 0.091667 | 0.089583 | 0.088194 | 0.086111 | 0.084722 | 0.083333 | 0.081944
| 18.5 | 0.10833 | 0.10556 | 0.10278 | 0.1 | 0.097222 | 0.095139 | 0.093056 | 0.090972 | 0.088889 | 0.086806 | 0.084722 | 0.083333 | 0.08125 | 0.079861 | 0.078472 | 0.077083 | 0.075694
| 19 | 0.10069 | 0.097917 | 0.095139 | 0.092361 | 0.090278 | 0.088194 | 0.086111 | 0.084028 | 0.082639 | 0.080556 | 0.079167 | 0.077083 | 0.075694 | 0.074306 | 0.072917 | 0.071528 | 0.070139
| 19.5 | 0.09375 | 0.090972 | 0.088889 | 0.086806 | 0.084722 | 0.082639 | 0.080556 | 0.078472 | 0.077083 | 0.075694 | 0.073611 | 0.072222 | 0.070833 | 0.069444 | 0.099 | 0.097 | 0.095
| 20 | 0.0875 | 0.085417 | 0.083333 | 0.08125 | 0.079167 | 0.077778 | 0.075694 | 0.074306 | 0.072222 | 0.070833 | 0.069444 | 0.098 | 0.096 | 0.094 | 0.093 | 0.091 | 0.089
| 20.5 | 0.082639 | 0.080556 | 0.078472 | 0.076389 | 0.075 | 0.072917 | 0.071528 | 0.070139 | 0.099 | 0.097 | 0.095 | 0.093 | 0.091 | 0.089 | 0.088 | 0.086 | 0.085
| 21 | 0.078472 | 0.076389 | 0.074306 | 0.072917 | 0.070833 | 0.069444 | 0.098 | 0.096 | 0.094 | 0.092 | 0.09 | 0.088 | 0.086 | 0.085 | 0.083 | 0.082 | 0.081
| 21.5 | 0.075 | 0.072917 | 0.070833 | 0.069444 | 0.098 | 0.095 | 0.093 | 0.091 | 0.089 | 0.088 | 0.086 | 0.084 | 0.083 | 0.081 | 0.08 | 0.078 | 0.077
| 22 | 0.071528 | 0.070139 | 0.098 | 0.096 | 0.093 | 0.091 | 0.089 | 0.087 | 0.086 | 0.084 | 0.082 | 0.081 | 0.079 | 0.078 | 0.076 | 0.075 | 0.074
| 22.5 | 0.095 | 0.094 | 0.091 | 0.089 | 0.086 | 0.084 | 0.083 | 0.081 | 0.08 | 0.078 | 0.076 | 0.075 | 0.073 | 0.072 | 0.07 | 0.07 | 0.069
| 23 | 0.088 | 0.087 | 0.084 | 0.082 | 0.08 | 0.078 | 0.076 | 0.075 | 0.074 | 0.072 | 0.07 | 0.069 | 0.068 | 0.067 | 0.065 | 0.064 | 0.063
| 23.5 | 0.081 | 0.08 | 0.077 | 0.076 | 0.073 | 0.072 | 0.07 | 0.069 | 0.068 | 0.066 | 0.065 | 0.064 | 0.062 | 0.062 | 0.06 | 0.059 | 0.058
| 24 | 0.075 | 0.074 | 0.072 | 0.07 | 0.068 | 0.067 | 0.065 | 0.064 | 0.063 | 0.061 | 0.06 | 0.059 | 0.058 | 0.057 | 0.056 | 0.055 | 0.054
| 24.5 | 0.07 | 0.068 | 0.066 | 0.065 | 0.063 | 0.061 | 0.06 | 0.059 | 0.058 | 0.057 | 0.055 | 0.055 | 0.053 | 0.053 | 0.051 | 0.051 | 0.05
| 25 | 0.065 | 0.063 | 0.061 | 0.06 | 0.058 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053 | 0.051 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046
| 25.5 | 0.06 | 0.058 | 0.057 | 0.055 | 0.054 | 0.053 | 0.051 | 0.05 | 0.05 | 0.049 | 0.047 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.043
| 26 | 0.055 | 0.054 | 0.053 | 0.052 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.04