## Sheet1
PROPERTIES
General
Name | Nordex N149/5.X 5,18MW
Manufacturer | Nordex
Hub Height | 105 | 120 | 125 | 145 | 155 | 164
Power
Rated Power | 5180
Peak Power | 5180
Power Regulation Type | Pitch
Voltage | 750
Rotor
Rotor diameter | 149
Number of blades | 3
Rated RPM | 20.5
Rotor tilt | 6
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 26
Restart Wind Speed | 25.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 50
High Temperature Restart | 40
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | S
Values
Certification | IEC 3rd Edition
Vave | 7.5-9.5
Vref | 42
Design TI | 0.11

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 2 | 4 | 5 | 8 | 10 | 12 | 13 | 16 | 18 | 20 | 23 | 24 | 26 | 29 | 31 | 33 | 34
| 3.5 | 66 | 70 | 73 | 77 | 80 | 84 | 87 | 91 | 95 | 98 | 102 | 105 | 109 | 113 | 116 | 120 | 123
| 4 | 155 | 161 | 167 | 173 | 179 | 185 | 191 | 197 | 203 | 209 | 215 | 221 | 227 | 233 | 239 | 246 | 252
| 4.5 | 264 | 273 | 283 | 292 | 301 | 310 | 319 | 328 | 337 | 346 | 355 | 364 | 374 | 383 | 392 | 401 | 410
| 5 | 396 | 409 | 421 | 434 | 447 | 460 | 472 | 485 | 498 | 510 | 523 | 536 | 549 | 561 | 574 | 587 | 600
| 5.5 | 552 | 569 | 586 | 603 | 620 | 637 | 654 | 671 | 688 | 705 | 722 | 739 | 756 | 773 | 790 | 807 | 824
| 6 | 736 | 758 | 780 | 802 | 824 | 847 | 869 | 891 | 913 | 935 | 957 | 979 | 1001 | 1023 | 1045 | 1068 | 1090
| 6.5 | 952 | 980 | 1008 | 1037 | 1065 | 1093 | 1121 | 1149 | 1177 | 1205 | 1233 | 1261 | 1289 | 1317 | 1345 | 1373 | 1401
| 7 | 1204 | 1239 | 1274 | 1309 | 1344 | 1379 | 1414 | 1449 | 1483 | 1518 | 1553 | 1588 | 1623 | 1658 | 1693 | 1728 | 1763
| 7.5 | 1494 | 1537 | 1580 | 1623 | 1665 | 1708 | 1751 | 1794 | 1837 | 1880 | 1923 | 1965 | 2008 | 2051 | 2094 | 2136 | 2179
| 8 | 1816 | 1868 | 1919 | 1971 | 2023 | 2074 | 2126 | 2178 | 2229 | 2281 | 2332 | 2384 | 2435 | 2487 | 2538 | 2590 | 2641
| 8.5 | 2150 | 2211 | 2272 | 2333 | 2394 | 2455 | 2515 | 2576 | 2637 | 2697 | 2758 | 2819 | 2879 | 2940 | 3000 | 3060 | 3121
| 9 | 2483 | 2553 | 2623 | 2693 | 2763 | 2832 | 2902 | 2972 | 3041 | 3111 | 3180 | 3250 | 3319 | 3389 | 3458 | 3527 | 3597
| 9.5 | 2804 | 2883 | 2962 | 3040 | 3119 | 3197 | 3275 | 3354 | 3432 | 3510 | 3588 | 3666 | 3745 | 3823 | 3902 | 3979 | 4054
| 10 | 3109 | 3196 | 3282 | 3369 | 3456 | 3543 | 3629 | 3715 | 3802 | 3888 | 3976 | 4063 | 4146 | 4227 | 4309 | 4384 | 4446
| 10.5 | 3397 | 3491 | 3586 | 3681 | 3775 | 3869 | 3963 | 4058 | 4154 | 4244 | 4331 | 4418 | 4490 | 4557 | 4624 | 4686 | 4735
| 11 | 3672 | 3775 | 3877 | 3978 | 4080 | 4183 | 4284 | 4376 | 4467 | 4546 | 4617 | 4688 | 4747 | 4801 | 4854 | 4902 | 4939
| 11.5 | 3940 | 4049 | 4158 | 4268 | 4372 | 4468 | 4560 | 4635 | 4711 | 4775 | 4832 | 4889 | 4934 | 4974 | 5014 | 5049 | 5074
| 12 | 4200 | 4316 | 4426 | 4526 | 4617 | 4697 | 4773 | 4834 | 4895 | 4944 | 4988 | 5031 | 5063 | 5090 | 5117 | 5139 | 5150
| 12.5 | 4450 | 4554 | 4650 | 4733 | 4808 | 4873 | 4934 | 4981 | 5027 | 5063 | 5093 | 5123 | 5141 | 5155 | 5169 | 5178 | 5179
| 13 | 4659 | 4746 | 4825 | 4893 | 4954 | 5003 | 5050 | 5083 | 5115 | 5138 | 5154 | 5171 | 5176 | 5178 | 5180 | 5180 | 5180
| 13.5 | 4825 | 4896 | 4960 | 5013 | 5059 | 5094 | 5127 | 5146 | 5165 | 5174 | 5177 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180
| 14 | 4954 | 5010 | 5059 | 5098 | 5129 | 5151 | 5170 | 5175 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180
| 14.5 | 5051 | 5092 | 5127 | 5151 | 5169 | 5176 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180
| 15 | 5119 | 5146 | 5166 | 5176 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180
| 15.5 | 5161 | 5173 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180
| 16 | 5179 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180
| 16.5 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180
| 17 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180
| 17.5 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180
| 18 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180
| 18.5 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180
| 19 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180
| 19.5 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180
| 20 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180
| 20.5 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180
| 21 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180
| 21.5 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180
| 22 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180
| 22.5 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180
| 23 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180
| 23.5 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180 | 5180
| 24 | 5178 | 5178 | 5178 | 5178 | 5178 | 5178 | 5178 | 5178 | 5178 | 5178 | 5178 | 5178 | 5178 | 5178 | 5178 | 5178 | 5178
| 24.5 | 5125 | 5125 | 5125 | 5125 | 5125 | 5125 | 5125 | 5125 | 5125 | 5125 | 5125 | 5125 | 5125 | 5125 | 5125 | 5125 | 5125
| 25 | 5039 | 5039 | 5039 | 5039 | 5039 | 5039 | 5039 | 5039 | 5039 | 5039 | 5039 | 5039 | 5039 | 5039 | 5039 | 5039 | 5039
| 25.5 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891
| 26 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986
| 3.5 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292
| 4 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597
| 4.5 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972
| 5 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417
| 5.5 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069
| 6 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861
| 6.5 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722
| 7 | 0.54514 | 0.54514 | 0.54514 | 0.54514 | 0.54514 | 0.54514 | 0.54514 | 0.54514 | 0.54514 | 0.54514 | 0.54514 | 0.54514 | 0.54514 | 0.54514 | 0.54514 | 0.54514 | 0.54514
| 7.5 | 0.53403 | 0.53403 | 0.53403 | 0.53403 | 0.53403 | 0.53403 | 0.53403 | 0.53403 | 0.53403 | 0.53403 | 0.53403 | 0.53403 | 0.53403 | 0.53403 | 0.53403 | 0.53403 | 0.53403
| 8 | 0.51597 | 0.51597 | 0.51597 | 0.51597 | 0.51597 | 0.51597 | 0.51597 | 0.51597 | 0.51597 | 0.51597 | 0.51597 | 0.51597 | 0.51597 | 0.51597 | 0.51597 | 0.51597 | 0.51597
| 8.5 | 0.49306 | 0.49306 | 0.49306 | 0.49306 | 0.49306 | 0.49306 | 0.49306 | 0.49306 | 0.49306 | 0.49306 | 0.49306 | 0.49306 | 0.49306 | 0.49306 | 0.49306 | 0.49306 | 0.49306
| 9 | 0.46736 | 0.46736 | 0.46736 | 0.46736 | 0.46736 | 0.46736 | 0.46736 | 0.46736 | 0.46736 | 0.46736 | 0.46736 | 0.46736 | 0.46736 | 0.46667 | 0.46667 | 0.46667 | 0.46667
| 9.5 | 0.43958 | 0.43958 | 0.43958 | 0.43958 | 0.43958 | 0.43958 | 0.43958 | 0.43958 | 0.43958 | 0.43958 | 0.43958 | 0.43958 | 0.43889 | 0.43819 | 0.4375 | 0.43611 | 0.43472
| 10 | 0.41181 | 0.41181 | 0.41181 | 0.41181 | 0.41181 | 0.41181 | 0.41181 | 0.41181 | 0.41111 | 0.41111 | 0.40972 | 0.40903 | 0.40764 | 0.40625 | 0.40486 | 0.40278 | 0.40139
| 10.5 | 0.38403 | 0.38403 | 0.38403 | 0.38403 | 0.38403 | 0.38333 | 0.38264 | 0.38194 | 0.38125 | 0.37986 | 0.37847 | 0.37639 | 0.375 | 0.37292 | 0.37083 | 0.36944 | 0.36736
| 11 | 0.35556 | 0.35556 | 0.35556 | 0.35556 | 0.35486 | 0.35347 | 0.35278 | 0.35139 | 0.34931 | 0.34792 | 0.34583 | 0.34375 | 0.34236 | 0.33958 | 0.3375 | 0.33542 | 0.33264
| 11.5 | 0.32778 | 0.32778 | 0.32708 | 0.32569 | 0.325 | 0.32361 | 0.32153 | 0.32014 | 0.31806 | 0.31597 | 0.31389 | 0.31181 | 0.30972 | 0.30694 | 0.30417 | 0.30208 | 0.29931
| 12 | 0.30139 | 0.30069 | 0.29931 | 0.29792 | 0.29653 | 0.29444 | 0.29236 | 0.29028 | 0.28819 | 0.28611 | 0.28333 | 0.28125 | 0.27847 | 0.27639 | 0.27361 | 0.27083 | 0.26806
| 12.5 | 0.27708 | 0.27569 | 0.27431 | 0.27222 | 0.27083 | 0.26875 | 0.26667 | 0.26389 | 0.26181 | 0.25903 | 0.25694 | 0.25417 | 0.25139 | 0.24861 | 0.24583 | 0.24306 | 0.24028
| 13 | 0.25486 | 0.25347 | 0.25139 | 0.24931 | 0.24722 | 0.24514 | 0.24236 | 0.24028 | 0.2375 | 0.23542 | 0.23264 | 0.22986 | 0.22708 | 0.22431 | 0.22153 | 0.21875 | 0.21528
| 13.5 | 0.23472 | 0.23264 | 0.23056 | 0.22847 | 0.22639 | 0.22361 | 0.22083 | 0.21875 | 0.21597 | 0.21319 | 0.21042 | 0.20764 | 0.20486 | 0.20208 | 0.19931 | 0.19653 | 0.19306
| 14 | 0.21597 | 0.21389 | 0.21181 | 0.20903 | 0.20694 | 0.20417 | 0.20139 | 0.19931 | 0.19653 | 0.19375 | 0.19097 | 0.18819 | 0.18542 | 0.18194 | 0.17917 | 0.17639 | 0.17361
| 14.5 | 0.19861 | 0.19653 | 0.19444 | 0.19167 | 0.18958 | 0.18681 | 0.18403 | 0.18125 | 0.17847 | 0.17569 | 0.17292 | 0.17014 | 0.16736 | 0.16389 | 0.16111 | 0.15833 | 0.15556
| 15 | 0.18333 | 0.18125 | 0.17847 | 0.17569 | 0.17361 | 0.17083 | 0.16806 | 0.16528 | 0.1625 | 0.15972 | 0.15694 | 0.15347 | 0.15069 | 0.14792 | 0.14514 | 0.14236 | 0.13958
| 15.5 | 0.16875 | 0.16667 | 0.16389 | 0.16181 | 0.15903 | 0.15625 | 0.15347 | 0.15069 | 0.14792 | 0.14514 | 0.14167 | 0.13889 | 0.13611 | 0.13333 | 0.13056 | 0.12778 | 0.12569
| 16 | 0.15625 | 0.15347 | 0.15069 | 0.14792 | 0.14583 | 0.14306 | 0.14028 | 0.1375 | 0.13403 | 0.13125 | 0.12847 | 0.12569 | 0.12292 | 0.12083 | 0.11806 | 0.11597 | 0.11319
| 16.5 | 0.14375 | 0.14167 | 0.13889 | 0.13611 | 0.13333 | 0.13056 | 0.12778 | 0.125 | 0.12222 | 0.11944 | 0.11667 | 0.11389 | 0.11181 | 0.10972 | 0.10764 | 0.10556 | 0.10347
| 17 | 0.13264 | 0.13056 | 0.12778 | 0.125 | 0.12222 | 0.11944 | 0.11667 | 0.11389 | 0.11111 | 0.10903 | 0.10625 | 0.10417 | 0.10208 | 0.1 | 0.097917 | 0.095833 | 0.094444
| 17.5 | 0.12292 | 0.12014 | 0.11736 | 0.11458 | 0.11181 | 0.10903 | 0.10694 | 0.10417 | 0.10208 | 0.099306 | 0.097222 | 0.095139 | 0.09375 | 0.091667 | 0.089583 | 0.088194 | 0.086806
| 18 | 0.11389 | 0.11111 | 0.10833 | 0.10556 | 0.10278 | 0.1 | 0.097917 | 0.095833 | 0.09375 | 0.091667 | 0.089583 | 0.0875 | 0.086111 | 0.084028 | 0.082639 | 0.08125 | 0.079861
| 18.5 | 0.10556 | 0.10278 | 0.1 | 0.097222 | 0.095139 | 0.092361 | 0.090278 | 0.088194 | 0.086806 | 0.084722 | 0.082639 | 0.08125 | 0.079861 | 0.077778 | 0.076389 | 0.075 | 0.073611
| 19 | 0.097917 | 0.095139 | 0.093056 | 0.090278 | 0.088194 | 0.086111 | 0.084028 | 0.081944 | 0.080556 | 0.078472 | 0.077083 | 0.075694 | 0.074306 | 0.072917 | 0.071528 | 0.070139 | 0.099
| 19.5 | 0.091667 | 0.088889 | 0.086806 | 0.084722 | 0.082639 | 0.080556 | 0.078472 | 0.077083 | 0.075 | 0.073611 | 0.072222 | 0.070833 | 0.069444 | 0.098 | 0.096 | 0.094 | 0.093
| 20 | 0.085417 | 0.083333 | 0.08125 | 0.079167 | 0.077083 | 0.075694 | 0.073611 | 0.072222 | 0.070833 | 0.069444 | 0.098 | 0.096 | 0.094 | 0.092 | 0.091 | 0.089 | 0.087
| 20.5 | 0.080556 | 0.078472 | 0.077083 | 0.075 | 0.072917 | 0.071528 | 0.070139 | 0.098 | 0.096 | 0.094 | 0.092 | 0.091 | 0.089 | 0.087 | 0.086 | 0.084 | 0.083
| 21 | 0.076389 | 0.075 | 0.072917 | 0.070833 | 0.069444 | 0.098 | 0.095 | 0.093 | 0.091 | 0.09 | 0.088 | 0.086 | 0.084 | 0.083 | 0.081 | 0.08 | 0.079
| 21.5 | 0.072917 | 0.071528 | 0.069444 | 0.098 | 0.095 | 0.093 | 0.091 | 0.089 | 0.087 | 0.085 | 0.084 | 0.082 | 0.081 | 0.079 | 0.078 | 0.076 | 0.075
| 22 | 0.070139 | 0.098 | 0.096 | 0.093 | 0.091 | 0.089 | 0.087 | 0.085 | 0.084 | 0.082 | 0.08 | 0.079 | 0.077 | 0.076 | 0.075 | 0.073 | 0.072
| 22.5 | 0.094 | 0.091 | 0.089 | 0.086 | 0.084 | 0.083 | 0.081 | 0.079 | 0.078 | 0.076 | 0.074 | 0.073 | 0.071 | 0.07 | 0.07 | 0.068 | 0.067
| 23 | 0.087 | 0.084 | 0.082 | 0.08 | 0.078 | 0.076 | 0.075 | 0.073 | 0.072 | 0.07 | 0.069 | 0.068 | 0.066 | 0.065 | 0.064 | 0.063 | 0.062
| 23.5 | 0.08 | 0.077 | 0.076 | 0.073 | 0.072 | 0.07 | 0.069 | 0.067 | 0.066 | 0.065 | 0.063 | 0.062 | 0.061 | 0.06 | 0.059 | 0.058 | 0.057
| 24 | 0.074 | 0.072 | 0.07 | 0.068 | 0.067 | 0.065 | 0.064 | 0.062 | 0.061 | 0.06 | 0.059 | 0.058 | 0.056 | 0.056 | 0.055 | 0.053 | 0.053
| 24.5 | 0.068 | 0.066 | 0.065 | 0.063 | 0.061 | 0.06 | 0.059 | 0.057 | 0.057 | 0.055 | 0.054 | 0.053 | 0.052 | 0.051 | 0.051 | 0.049 | 0.049
| 25 | 0.063 | 0.061 | 0.06 | 0.058 | 0.057 | 0.056 | 0.055 | 0.053 | 0.053 | 0.051 | 0.05 | 0.05 | 0.048 | 0.048 | 0.047 | 0.046 | 0.045
| 25.5 | 0.058 | 0.057 | 0.055 | 0.054 | 0.053 | 0.051 | 0.05 | 0.049 | 0.049 | 0.047 | 0.046 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.042
| 26 | 0.054 | 0.053 | 0.052 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.043 | 0.041 | 0.041 | 0.04 | 0.039 | 0.039