## Sheet1
PROPERTIES
General
Name | Nordex N149/5.X 5,06MW
Manufacturer | Nordex
Hub Height | 105 | 120 | 125 | 155 | 164
Power
Rated Power | 5060
Peak Power | 5060
Power Regulation Type | Pitch
Voltage | 750
Rotor
Rotor diameter | 149
Number of blades | 3
Rated RPM | 20.5
Rotor tilt | 6
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 26
Restart Wind Speed | 25.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 50
High Temperature Restart | 40
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | S
Values
Certification | IEC 3rd Edition
Vave | 7.5-9.5
Vref | 42
Design TI | 0.11

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 2 | 4 | 5 | 8 | 10 | 12 | 13 | 16 | 18 | 20 | 23 | 24 | 26 | 29 | 31 | 33 | 34
| 3.5 | 66 | 70 | 73 | 77 | 80 | 84 | 87 | 91 | 95 | 98 | 102 | 105 | 109 | 113 | 116 | 120 | 123
| 4 | 155 | 161 | 167 | 173 | 179 | 185 | 191 | 197 | 203 | 209 | 215 | 221 | 227 | 233 | 239 | 246 | 252
| 4.5 | 264 | 273 | 283 | 292 | 301 | 310 | 319 | 328 | 337 | 346 | 355 | 364 | 374 | 383 | 392 | 401 | 410
| 5 | 396 | 409 | 421 | 434 | 447 | 460 | 472 | 485 | 498 | 510 | 523 | 536 | 549 | 561 | 574 | 587 | 600
| 5.5 | 552 | 569 | 586 | 603 | 620 | 637 | 654 | 671 | 688 | 705 | 722 | 739 | 756 | 773 | 790 | 807 | 824
| 6 | 736 | 758 | 780 | 802 | 824 | 847 | 869 | 891 | 913 | 935 | 957 | 979 | 1001 | 1023 | 1045 | 1068 | 1090
| 6.5 | 952 | 980 | 1008 | 1037 | 1065 | 1093 | 1121 | 1149 | 1177 | 1205 | 1233 | 1261 | 1289 | 1317 | 1345 | 1373 | 1401
| 7 | 1204 | 1239 | 1274 | 1309 | 1344 | 1379 | 1414 | 1449 | 1483 | 1518 | 1553 | 1588 | 1623 | 1658 | 1693 | 1728 | 1763
| 7.5 | 1493 | 1536 | 1579 | 1622 | 1665 | 1707 | 1750 | 1793 | 1836 | 1879 | 1922 | 1964 | 2007 | 2050 | 2093 | 2135 | 2178
| 8 | 1808 | 1860 | 1911 | 1963 | 2014 | 2066 | 2117 | 2168 | 2220 | 2271 | 2322 | 2374 | 2425 | 2476 | 2528 | 2579 | 2630
| 8.5 | 2129 | 2190 | 2250 | 2310 | 2370 | 2430 | 2491 | 2551 | 2611 | 2671 | 2731 | 2791 | 2851 | 2911 | 2971 | 3031 | 3090
| 9 | 2445 | 2514 | 2582 | 2651 | 2720 | 2789 | 2857 | 2926 | 2995 | 3063 | 3132 | 3200 | 3269 | 3337 | 3405 | 3474 | 3542
| 9.5 | 2747 | 2824 | 2901 | 2978 | 3055 | 3132 | 3209 | 3285 | 3362 | 3439 | 3515 | 3592 | 3668 | 3745 | 3822 | 3899 | 3973
| 10 | 3031 | 3116 | 3201 | 3286 | 3370 | 3455 | 3539 | 3624 | 3708 | 3792 | 3877 | 3962 | 4045 | 4125 | 4205 | 4284 | 4346
| 10.5 | 3302 | 3394 | 3486 | 3578 | 3670 | 3761 | 3853 | 3945 | 4038 | 4129 | 4214 | 4298 | 4377 | 4442 | 4507 | 4573 | 4622
| 11 | 3562 | 3661 | 3760 | 3859 | 3958 | 4057 | 4157 | 4249 | 4338 | 4423 | 4493 | 4562 | 4626 | 4678 | 4730 | 4782 | 4819
| 11.5 | 3815 | 3921 | 4026 | 4133 | 4239 | 4333 | 4426 | 4505 | 4578 | 4648 | 4704 | 4759 | 4810 | 4849 | 4888 | 4926 | 4951
| 12 | 4062 | 4175 | 4287 | 4385 | 4482 | 4560 | 4637 | 4701 | 4760 | 4816 | 4858 | 4900 | 4937 | 4964 | 4990 | 5016 | 5028
| 12.5 | 4303 | 4409 | 4509 | 4592 | 4672 | 4736 | 4798 | 4848 | 4893 | 4935 | 4964 | 4993 | 5017 | 5031 | 5044 | 5057 | 5059
| 13 | 4511 | 4602 | 4686 | 4753 | 4819 | 4868 | 4916 | 4952 | 4984 | 5012 | 5028 | 5044 | 5056 | 5058 | 5059 | 5060 | 5060
| 13.5 | 4679 | 4754 | 4822 | 4875 | 4926 | 4962 | 4996 | 5019 | 5038 | 5053 | 5056 | 5059 | 5060 | 5060 | 5060 | 5060 | 5060
| 14 | 4811 | 4870 | 4925 | 4963 | 5000 | 5022 | 5043 | 5053 | 5058 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060
| 14.5 | 4911 | 4957 | 4996 | 5021 | 5045 | 5053 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060
| 15 | 4983 | 5015 | 5041 | 5051 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060
| 15.5 | 5031 | 5048 | 5059 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060
| 16 | 5055 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060
| 16.5 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060
| 17 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060
| 17.5 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060
| 18 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060
| 18.5 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060
| 19 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060
| 19.5 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060
| 20 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060
| 20.5 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060
| 21 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060
| 21.5 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060
| 22 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060
| 22.5 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060
| 23 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060
| 23.5 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060
| 24 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060 | 5060
| 24.5 | 5056 | 5056 | 5056 | 5056 | 5056 | 5056 | 5056 | 5056 | 5056 | 5056 | 5056 | 5056 | 5056 | 5056 | 5056 | 5056 | 5056
| 25 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012
| 25.5 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891
| 26 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986
| 3.5 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292
| 4 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597
| 4.5 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972
| 5 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417
| 5.5 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069
| 6 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861
| 6.5 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722
| 7 | 0.54236 | 0.54236 | 0.54236 | 0.54236 | 0.54236 | 0.54236 | 0.54236 | 0.54236 | 0.54236 | 0.54236 | 0.54236 | 0.54236 | 0.54236 | 0.54236 | 0.54236 | 0.54236 | 0.54236
| 7.5 | 0.52778 | 0.52778 | 0.52778 | 0.52778 | 0.52778 | 0.52778 | 0.52778 | 0.52778 | 0.52778 | 0.52778 | 0.52778 | 0.52778 | 0.52778 | 0.52778 | 0.52778 | 0.52778 | 0.52778
| 8 | 0.50764 | 0.50764 | 0.50764 | 0.50764 | 0.50764 | 0.50764 | 0.50764 | 0.50764 | 0.50764 | 0.50764 | 0.50764 | 0.50764 | 0.50764 | 0.50764 | 0.50764 | 0.50764 | 0.50764
| 8.5 | 0.48264 | 0.48264 | 0.48264 | 0.48264 | 0.48264 | 0.48264 | 0.48264 | 0.48264 | 0.48264 | 0.48264 | 0.48264 | 0.48264 | 0.48264 | 0.48264 | 0.48264 | 0.48264 | 0.48264
| 9 | 0.45556 | 0.45556 | 0.45556 | 0.45556 | 0.45556 | 0.45556 | 0.45556 | 0.45556 | 0.45556 | 0.45556 | 0.45556 | 0.45556 | 0.45556 | 0.45556 | 0.45556 | 0.45556 | 0.45556
| 9.5 | 0.42778 | 0.42778 | 0.42778 | 0.42778 | 0.42778 | 0.42778 | 0.42778 | 0.42778 | 0.42778 | 0.42778 | 0.42778 | 0.42708 | 0.42708 | 0.42639 | 0.42569 | 0.42431 | 0.42361
| 10 | 0.39861 | 0.39861 | 0.39861 | 0.39861 | 0.39861 | 0.39861 | 0.39861 | 0.39931 | 0.39861 | 0.39792 | 0.39792 | 0.39653 | 0.39583 | 0.39444 | 0.39306 | 0.39167 | 0.39028
| 10.5 | 0.37014 | 0.37014 | 0.37014 | 0.37014 | 0.37014 | 0.37014 | 0.36944 | 0.36875 | 0.36806 | 0.36736 | 0.36597 | 0.36458 | 0.3625 | 0.36111 | 0.35903 | 0.35764 | 0.35556
| 11 | 0.34167 | 0.34167 | 0.34167 | 0.34167 | 0.34097 | 0.34028 | 0.33958 | 0.33819 | 0.33681 | 0.33542 | 0.33333 | 0.33194 | 0.32986 | 0.32778 | 0.32569 | 0.32361 | 0.32153
| 11.5 | 0.31458 | 0.31458 | 0.31389 | 0.31319 | 0.3125 | 0.31111 | 0.30972 | 0.30833 | 0.30625 | 0.30417 | 0.30278 | 0.3 | 0.29792 | 0.29583 | 0.29375 | 0.29097 | 0.28889
| 12 | 0.28958 | 0.28889 | 0.2875 | 0.28681 | 0.28542 | 0.28403 | 0.28194 | 0.27986 | 0.27778 | 0.27569 | 0.27361 | 0.27153 | 0.26875 | 0.26667 | 0.26389 | 0.26111 | 0.25903
| 12.5 | 0.26667 | 0.26528 | 0.26389 | 0.2625 | 0.26042 | 0.25903 | 0.25694 | 0.25486 | 0.25278 | 0.25 | 0.24792 | 0.24514 | 0.24306 | 0.24028 | 0.2375 | 0.23472 | 0.23264
| 13 | 0.24514 | 0.24375 | 0.24236 | 0.24028 | 0.23819 | 0.23681 | 0.23403 | 0.23194 | 0.22986 | 0.22708 | 0.225 | 0.22222 | 0.21944 | 0.21667 | 0.21389 | 0.21111 | 0.20903
| 13.5 | 0.22639 | 0.22431 | 0.22222 | 0.22014 | 0.21806 | 0.21597 | 0.21389 | 0.21111 | 0.20903 | 0.20625 | 0.20417 | 0.20139 | 0.19861 | 0.19583 | 0.19306 | 0.19028 | 0.1875
| 14 | 0.20833 | 0.20625 | 0.20417 | 0.20208 | 0.2 | 0.19792 | 0.19514 | 0.19236 | 0.19028 | 0.1875 | 0.18472 | 0.18194 | 0.17917 | 0.17708 | 0.17361 | 0.17083 | 0.16875
| 14.5 | 0.19236 | 0.19028 | 0.1875 | 0.18542 | 0.18333 | 0.18056 | 0.17847 | 0.17569 | 0.17292 | 0.17014 | 0.16806 | 0.16528 | 0.1625 | 0.15972 | 0.15694 | 0.15417 | 0.15139
| 15 | 0.17708 | 0.175 | 0.17292 | 0.17014 | 0.16806 | 0.16528 | 0.1625 | 0.16042 | 0.15764 | 0.15486 | 0.15208 | 0.14931 | 0.14653 | 0.14375 | 0.14097 | 0.13819 | 0.13542
| 15.5 | 0.16389 | 0.16111 | 0.15903 | 0.15625 | 0.15417 | 0.15139 | 0.14861 | 0.14653 | 0.14375 | 0.14097 | 0.13819 | 0.13542 | 0.13264 | 0.12986 | 0.12708 | 0.12431 | 0.12222
| 16 | 0.15139 | 0.14861 | 0.14653 | 0.14375 | 0.14097 | 0.13889 | 0.13611 | 0.13333 | 0.13056 | 0.12778 | 0.12569 | 0.12292 | 0.12014 | 0.11736 | 0.11528 | 0.1125 | 0.11042
| 16.5 | 0.13958 | 0.1375 | 0.13472 | 0.13194 | 0.12986 | 0.12708 | 0.12431 | 0.12153 | 0.11875 | 0.11667 | 0.11389 | 0.11111 | 0.10903 | 0.10694 | 0.10486 | 0.10278 | 0.10069
| 17 | 0.12917 | 0.12639 | 0.12431 | 0.12153 | 0.11875 | 0.11667 | 0.11389 | 0.11111 | 0.10833 | 0.10625 | 0.10347 | 0.10139 | 0.099306 | 0.097222 | 0.095833 | 0.09375 | 0.091667
| 17.5 | 0.11944 | 0.11667 | 0.11458 | 0.11181 | 0.10903 | 0.10694 | 0.10417 | 0.10139 | 0.099306 | 0.097222 | 0.095139 | 0.093056 | 0.090972 | 0.089583 | 0.0875 | 0.086111 | 0.084028
| 18 | 0.11042 | 0.10833 | 0.10556 | 0.10278 | 0.1 | 0.097917 | 0.095833 | 0.093056 | 0.090972 | 0.089583 | 0.0875 | 0.085417 | 0.084028 | 0.081944 | 0.080556 | 0.079167 | 0.077778
| 18.5 | 0.10278 | 0.1 | 0.097222 | 0.095139 | 0.092361 | 0.090278 | 0.088194 | 0.086111 | 0.084722 | 0.082639 | 0.080556 | 0.079167 | 0.077778 | 0.076389 | 0.075 | 0.073611 | 0.072222
| 19 | 0.095833 | 0.093056 | 0.090278 | 0.088194 | 0.086111 | 0.084028 | 0.081944 | 0.080556 | 0.078472 | 0.077083 | 0.075 | 0.073611 | 0.072222 | 0.070833 | 0.069444 | 0.098 | 0.097
| 19.5 | 0.088889 | 0.086806 | 0.084722 | 0.082639 | 0.080556 | 0.078472 | 0.077083 | 0.075 | 0.073611 | 0.072222 | 0.070139 | 0.099 | 0.097 | 0.096 | 0.094 | 0.092 | 0.091
| 20 | 0.084028 | 0.08125 | 0.079167 | 0.077083 | 0.075694 | 0.073611 | 0.072222 | 0.070833 | 0.099 | 0.097 | 0.095 | 0.094 | 0.092 | 0.09 | 0.088 | 0.087 | 0.085
| 20.5 | 0.079167 | 0.077083 | 0.075 | 0.072917 | 0.071528 | 0.069444 | 0.098 | 0.096 | 0.094 | 0.092 | 0.09 | 0.088 | 0.087 | 0.085 | 0.084 | 0.082 | 0.081
| 21 | 0.075 | 0.072917 | 0.070833 | 0.069444 | 0.098 | 0.095 | 0.093 | 0.091 | 0.089 | 0.087 | 0.086 | 0.084 | 0.082 | 0.081 | 0.079 | 0.078 | 0.077
| 21.5 | 0.071528 | 0.069444 | 0.098 | 0.095 | 0.093 | 0.091 | 0.089 | 0.087 | 0.085 | 0.083 | 0.082 | 0.08 | 0.079 | 0.077 | 0.076 | 0.075 | 0.073
| 22 | 0.098 | 0.096 | 0.094 | 0.091 | 0.089 | 0.087 | 0.085 | 0.083 | 0.082 | 0.08 | 0.078 | 0.077 | 0.076 | 0.074 | 0.073 | 0.072 | 0.07
| 22.5 | 0.091 | 0.089 | 0.087 | 0.084 | 0.083 | 0.081 | 0.079 | 0.077 | 0.076 | 0.074 | 0.072 | 0.071 | 0.07 | 0.069 | 0.068 | 0.067 | 0.065
| 23 | 0.084 | 0.082 | 0.081 | 0.078 | 0.076 | 0.075 | 0.073 | 0.071 | 0.07 | 0.069 | 0.067 | 0.066 | 0.065 | 0.063 | 0.063 | 0.062 | 0.06
| 23.5 | 0.077 | 0.076 | 0.074 | 0.072 | 0.07 | 0.069 | 0.067 | 0.066 | 0.065 | 0.063 | 0.062 | 0.061 | 0.06 | 0.058 | 0.058 | 0.057 | 0.055
| 24 | 0.072 | 0.07 | 0.069 | 0.067 | 0.065 | 0.064 | 0.062 | 0.061 | 0.06 | 0.059 | 0.057 | 0.056 | 0.056 | 0.054 | 0.053 | 0.053 | 0.051
| 24.5 | 0.066 | 0.065 | 0.063 | 0.061 | 0.06 | 0.059 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.049 | 0.047
| 25 | 0.061 | 0.06 | 0.059 | 0.057 | 0.056 | 0.055 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.048 | 0.046 | 0.046 | 0.045 | 0.044
| 25.5 | 0.057 | 0.055 | 0.054 | 0.053 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.045 | 0.044 | 0.043 | 0.042 | 0.042 | 0.04
| 26 | 0.053 | 0.052 | 0.051 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.041 | 0.04 | 0.039 | 0.039 | 0.038