## Sheet1
PROPERTIES
General
Name | Nordex N149/5.X 4,95MW
Manufacturer | Nordex
Hub Height | 105 | 120 | 125 | 164
Power
Rated Power | 4950
Peak Power | 4950
Power Regulation Type | Pitch
Voltage | 750
Rotor
Rotor diameter | 149
Number of blades | 3
Rated RPM | 20.5
Rotor tilt | 6
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 26
Restart Wind Speed | 25.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 50
High Temperature Restart | 40
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | S
Values
Certification | IEC 3rd Edition
Vave | 7.5-9.5
Vref | 42
Design TI | 0.11

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 2 | 4 | 5 | 8 | 10 | 12 | 13 | 16 | 18 | 20 | 23 | 24 | 26 | 29 | 31 | 33 | 34
| 3.5 | 66 | 70 | 73 | 77 | 80 | 84 | 87 | 91 | 95 | 98 | 102 | 105 | 109 | 113 | 116 | 120 | 123
| 4 | 155 | 161 | 167 | 173 | 179 | 185 | 191 | 197 | 203 | 209 | 215 | 221 | 227 | 233 | 239 | 246 | 252
| 4.5 | 264 | 273 | 283 | 292 | 301 | 310 | 319 | 328 | 337 | 346 | 355 | 364 | 374 | 383 | 392 | 401 | 410
| 5 | 396 | 409 | 421 | 434 | 447 | 460 | 472 | 485 | 498 | 510 | 523 | 536 | 549 | 561 | 574 | 587 | 600
| 5.5 | 552 | 569 | 586 | 603 | 620 | 637 | 654 | 671 | 688 | 705 | 722 | 739 | 756 | 773 | 790 | 807 | 824
| 6 | 736 | 758 | 780 | 802 | 825 | 847 | 869 | 891 | 913 | 935 | 957 | 979 | 1001 | 1023 | 1045 | 1068 | 1090
| 6.5 | 952 | 980 | 1008 | 1036 | 1065 | 1093 | 1121 | 1149 | 1177 | 1205 | 1233 | 1261 | 1289 | 1317 | 1345 | 1373 | 1401
| 7 | 1204 | 1239 | 1274 | 1309 | 1344 | 1379 | 1414 | 1449 | 1484 | 1519 | 1554 | 1588 | 1623 | 1658 | 1693 | 1728 | 1763
| 7.5 | 1491 | 1533 | 1576 | 1619 | 1662 | 1705 | 1748 | 1790 | 1833 | 1876 | 1919 | 1961 | 2004 | 2047 | 2089 | 2132 | 2175
| 8 | 1796 | 1847 | 1899 | 1950 | 2001 | 2052 | 2103 | 2154 | 2205 | 2256 | 2307 | 2358 | 2409 | 2460 | 2511 | 2562 | 2613
| 8.5 | 2103 | 2162 | 2222 | 2282 | 2341 | 2401 | 2460 | 2519 | 2579 | 2638 | 2697 | 2757 | 2816 | 2875 | 2934 | 2994 | 3053
| 9 | 2401 | 2468 | 2536 | 2604 | 2671 | 2739 | 2806 | 2874 | 2941 | 3009 | 3076 | 3143 | 3210 | 3278 | 3345 | 3412 | 3479
| 9.5 | 2683 | 2759 | 2834 | 2909 | 2985 | 3060 | 3135 | 3210 | 3285 | 3360 | 3435 | 3510 | 3584 | 3659 | 3735 | 3810 | 3884
| 10 | 2950 | 3032 | 3115 | 3197 | 3280 | 3362 | 3444 | 3527 | 3609 | 3690 | 3773 | 3856 | 3938 | 4017 | 4095 | 4172 | 4242
| 10.5 | 3204 | 3293 | 3383 | 3472 | 3561 | 3650 | 3739 | 3828 | 3918 | 4008 | 4093 | 4175 | 4258 | 4326 | 4389 | 4453 | 4509
| 11 | 3450 | 3546 | 3642 | 3738 | 3833 | 3929 | 4026 | 4121 | 4208 | 4294 | 4368 | 4436 | 4503 | 4558 | 4608 | 4659 | 4703
| 11.5 | 3689 | 3791 | 3894 | 3996 | 4099 | 4198 | 4288 | 4375 | 4446 | 4517 | 4577 | 4631 | 4685 | 4727 | 4765 | 4803 | 4834
| 12 | 3923 | 4032 | 4141 | 4245 | 4338 | 4425 | 4500 | 4572 | 4629 | 4686 | 4733 | 4774 | 4814 | 4844 | 4869 | 4895 | 4914
| 12.5 | 4153 | 4265 | 4362 | 4453 | 4531 | 4602 | 4663 | 4721 | 4765 | 4808 | 4842 | 4870 | 4898 | 4915 | 4928 | 4941 | 4948
| 13 | 4362 | 4460 | 4541 | 4617 | 4680 | 4738 | 4784 | 4829 | 4859 | 4890 | 4911 | 4926 | 4942 | 4947 | 4948 | 4950 | 4950
| 13.5 | 4533 | 4615 | 4682 | 4743 | 4792 | 4836 | 4869 | 4900 | 4918 | 4936 | 4945 | 4948 | 4950 | 4950 | 4950 | 4950 | 4950
| 14 | 4669 | 4736 | 4789 | 4836 | 4871 | 4902 | 4922 | 4940 | 4945 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950
| 14.5 | 4774 | 4828 | 4866 | 4899 | 4922 | 4939 | 4946 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950
| 15 | 4852 | 4892 | 4917 | 4936 | 4945 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950
| 15.5 | 4906 | 4932 | 4943 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950
| 16 | 4937 | 4949 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950
| 16.5 | 4949 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950
| 17 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950
| 17.5 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950
| 18 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950
| 18.5 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950
| 19 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950
| 19.5 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950
| 20 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950
| 20.5 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950
| 21 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950
| 21.5 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950
| 22 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950
| 22.5 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950
| 23 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950
| 23.5 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950
| 24 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950
| 24.5 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950 | 4950
| 25 | 4943 | 4943 | 4943 | 4943 | 4943 | 4943 | 4943 | 4943 | 4943 | 4943 | 4943 | 4943 | 4943 | 4943 | 4943 | 4943 | 4943
| 25.5 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891 | 4891
| 26 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986
| 3.5 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292
| 4 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597
| 4.5 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972
| 5 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417
| 5.5 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069
| 6 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861
| 6.5 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722 | 0.54722
| 7 | 0.53889 | 0.53889 | 0.53889 | 0.53889 | 0.53889 | 0.53889 | 0.53889 | 0.53889 | 0.53889 | 0.53889 | 0.53889 | 0.53889 | 0.53889 | 0.53889 | 0.53889 | 0.53889 | 0.53889
| 7.5 | 0.52153 | 0.52153 | 0.52153 | 0.52153 | 0.52153 | 0.52153 | 0.52153 | 0.52153 | 0.52153 | 0.52153 | 0.52153 | 0.52153 | 0.52153 | 0.52153 | 0.52153 | 0.52153 | 0.52153
| 8 | 0.49931 | 0.49931 | 0.49931 | 0.49931 | 0.49931 | 0.49931 | 0.49931 | 0.49931 | 0.49931 | 0.49931 | 0.49931 | 0.49931 | 0.49931 | 0.49931 | 0.49931 | 0.49931 | 0.49931
| 8.5 | 0.47292 | 0.47292 | 0.47292 | 0.47292 | 0.47292 | 0.47292 | 0.47292 | 0.47292 | 0.47292 | 0.47292 | 0.47292 | 0.47292 | 0.47292 | 0.47292 | 0.47292 | 0.47292 | 0.47292
| 9 | 0.44444 | 0.44444 | 0.44444 | 0.44444 | 0.44444 | 0.44444 | 0.44444 | 0.44444 | 0.44444 | 0.44444 | 0.44444 | 0.44444 | 0.44444 | 0.44444 | 0.44444 | 0.44444 | 0.44444
| 9.5 | 0.41528 | 0.41528 | 0.41528 | 0.41528 | 0.41528 | 0.41528 | 0.41528 | 0.41528 | 0.41528 | 0.41597 | 0.41597 | 0.41528 | 0.41528 | 0.41528 | 0.41458 | 0.41319 | 0.4125
| 10 | 0.38611 | 0.38611 | 0.38611 | 0.38611 | 0.38611 | 0.38611 | 0.38611 | 0.38611 | 0.38611 | 0.38611 | 0.38542 | 0.38472 | 0.38403 | 0.38264 | 0.38125 | 0.37986 | 0.37847
| 10.5 | 0.35694 | 0.35694 | 0.35694 | 0.35694 | 0.35694 | 0.35694 | 0.35694 | 0.35625 | 0.35556 | 0.35486 | 0.35347 | 0.35208 | 0.35069 | 0.34931 | 0.34792 | 0.34583 | 0.34444
| 11 | 0.32847 | 0.32847 | 0.32847 | 0.32847 | 0.32778 | 0.32708 | 0.32639 | 0.32569 | 0.32431 | 0.32292 | 0.32153 | 0.31944 | 0.31806 | 0.31597 | 0.31389 | 0.31181 | 0.31042
| 11.5 | 0.30208 | 0.30208 | 0.30139 | 0.30069 | 0.3 | 0.29861 | 0.29792 | 0.29653 | 0.29444 | 0.29306 | 0.29097 | 0.28958 | 0.2875 | 0.28542 | 0.28333 | 0.28056 | 0.27847
| 12 | 0.27847 | 0.27778 | 0.27639 | 0.27569 | 0.27431 | 0.27292 | 0.27153 | 0.26944 | 0.26806 | 0.26597 | 0.26389 | 0.26181 | 0.25972 | 0.25764 | 0.25486 | 0.25278 | 0.25
| 12.5 | 0.25625 | 0.25556 | 0.25417 | 0.25278 | 0.25139 | 0.24931 | 0.24792 | 0.24583 | 0.24375 | 0.24167 | 0.23958 | 0.23681 | 0.23472 | 0.23264 | 0.22986 | 0.22708 | 0.225
| 13 | 0.23611 | 0.23472 | 0.23333 | 0.23194 | 0.22986 | 0.22778 | 0.22639 | 0.22431 | 0.22222 | 0.21944 | 0.21736 | 0.21458 | 0.2125 | 0.20972 | 0.20764 | 0.20486 | 0.20208
| 13.5 | 0.21806 | 0.21597 | 0.21458 | 0.2125 | 0.21042 | 0.20833 | 0.20625 | 0.20417 | 0.20208 | 0.19931 | 0.19722 | 0.19514 | 0.19236 | 0.18958 | 0.1875 | 0.18472 | 0.18194
| 14 | 0.20069 | 0.19931 | 0.19722 | 0.19514 | 0.19306 | 0.19097 | 0.18889 | 0.18611 | 0.18403 | 0.18194 | 0.17917 | 0.17639 | 0.17431 | 0.17153 | 0.16875 | 0.16597 | 0.16389
| 14.5 | 0.18542 | 0.18333 | 0.18125 | 0.17917 | 0.17708 | 0.175 | 0.17292 | 0.17014 | 0.16806 | 0.16528 | 0.16319 | 0.16042 | 0.15764 | 0.15486 | 0.15278 | 0.15 | 0.14722
| 15 | 0.17153 | 0.16944 | 0.16736 | 0.16458 | 0.1625 | 0.16042 | 0.15764 | 0.15556 | 0.15278 | 0.15069 | 0.14792 | 0.14514 | 0.14306 | 0.14028 | 0.1375 | 0.13472 | 0.13194
| 15.5 | 0.15833 | 0.15625 | 0.15417 | 0.15139 | 0.14931 | 0.14722 | 0.14444 | 0.14236 | 0.13958 | 0.13681 | 0.13472 | 0.13194 | 0.12917 | 0.12639 | 0.12431 | 0.12153 | 0.11944
| 16 | 0.14653 | 0.14444 | 0.14167 | 0.13958 | 0.1375 | 0.13472 | 0.13264 | 0.12986 | 0.12708 | 0.125 | 0.12222 | 0.11944 | 0.11736 | 0.11458 | 0.1125 | 0.11042 | 0.10833
| 16.5 | 0.13542 | 0.13333 | 0.13056 | 0.12847 | 0.12639 | 0.12361 | 0.12153 | 0.11875 | 0.11597 | 0.11389 | 0.11111 | 0.10903 | 0.10625 | 0.10417 | 0.10208 | 0.1 | 0.098611
| 17 | 0.125 | 0.12292 | 0.12083 | 0.11806 | 0.11597 | 0.11319 | 0.11111 | 0.10833 | 0.10625 | 0.10347 | 0.10139 | 0.099306 | 0.097222 | 0.095139 | 0.093056 | 0.091667 | 0.089583
| 17.5 | 0.11597 | 0.11389 | 0.11111 | 0.10903 | 0.10625 | 0.10417 | 0.10139 | 0.099306 | 0.097222 | 0.095139 | 0.093056 | 0.090972 | 0.088889 | 0.0875 | 0.085417 | 0.084028 | 0.082639
| 18 | 0.10764 | 0.10486 | 0.10278 | 0.10069 | 0.097917 | 0.095833 | 0.093056 | 0.090972 | 0.088889 | 0.0875 | 0.085417 | 0.083333 | 0.081944 | 0.080556 | 0.078472 | 0.077083 | 0.075694
| 18.5 | 0.1 | 0.097917 | 0.095139 | 0.093056 | 0.090278 | 0.088194 | 0.086111 | 0.084028 | 0.082639 | 0.080556 | 0.079167 | 0.077083 | 0.075694 | 0.074306 | 0.072917 | 0.071528 | 0.070139
| 19 | 0.093056 | 0.090972 | 0.088194 | 0.086111 | 0.084028 | 0.081944 | 0.080556 | 0.078472 | 0.076389 | 0.075 | 0.073611 | 0.072222 | 0.070833 | 0.069444 | 0.098 | 0.096 | 0.094
| 19.5 | 0.0875 | 0.084722 | 0.082639 | 0.080556 | 0.078472 | 0.077083 | 0.075 | 0.073611 | 0.071528 | 0.070139 | 0.099 | 0.097 | 0.095 | 0.093 | 0.092 | 0.09 | 0.088
| 20 | 0.081944 | 0.079861 | 0.077778 | 0.075694 | 0.073611 | 0.072222 | 0.070833 | 0.099 | 0.097 | 0.095 | 0.093 | 0.091 | 0.09 | 0.088 | 0.086 | 0.085 | 0.083
| 20.5 | 0.077083 | 0.075 | 0.073611 | 0.071528 | 0.069444 | 0.098 | 0.096 | 0.094 | 0.092 | 0.09 | 0.088 | 0.086 | 0.085 | 0.083 | 0.082 | 0.08 | 0.079
| 21 | 0.072917 | 0.071528 | 0.069444 | 0.098 | 0.095 | 0.093 | 0.091 | 0.089 | 0.087 | 0.085 | 0.084 | 0.082 | 0.081 | 0.079 | 0.078 | 0.076 | 0.075
| 21.5 | 0.069444 | 0.098 | 0.095 | 0.093 | 0.091 | 0.089 | 0.087 | 0.085 | 0.083 | 0.082 | 0.08 | 0.078 | 0.077 | 0.076 | 0.074 | 0.073 | 0.072
| 22 | 0.096 | 0.094 | 0.091 | 0.089 | 0.087 | 0.085 | 0.083 | 0.082 | 0.08 | 0.078 | 0.077 | 0.075 | 0.074 | 0.073 | 0.071 | 0.07 | 0.069
| 22.5 | 0.089 | 0.087 | 0.084 | 0.083 | 0.081 | 0.079 | 0.077 | 0.076 | 0.074 | 0.072 | 0.071 | 0.07 | 0.069 | 0.068 | 0.066 | 0.065 | 0.064
| 23 | 0.082 | 0.081 | 0.078 | 0.076 | 0.075 | 0.073 | 0.071 | 0.07 | 0.069 | 0.067 | 0.066 | 0.064 | 0.063 | 0.063 | 0.061 | 0.06 | 0.059
| 23.5 | 0.076 | 0.074 | 0.072 | 0.07 | 0.069 | 0.067 | 0.066 | 0.065 | 0.063 | 0.062 | 0.061 | 0.059 | 0.058 | 0.058 | 0.056 | 0.055 | 0.055
| 24 | 0.07 | 0.069 | 0.067 | 0.065 | 0.064 | 0.062 | 0.061 | 0.06 | 0.059 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053 | 0.052 | 0.051 | 0.051
| 24.5 | 0.065 | 0.063 | 0.061 | 0.06 | 0.059 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.047
| 25 | 0.06 | 0.059 | 0.057 | 0.056 | 0.055 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.046 | 0.045 | 0.044 | 0.043
| 25.5 | 0.055 | 0.054 | 0.053 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.045 | 0.043 | 0.043 | 0.042 | 0.041 | 0.04 | 0.04
| 26 | 0.052 | 0.051 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.04 | 0.039 | 0.038 | 0.038 | 0.037