## Sheet1
PROPERTIES
General
Name | Nordex N149/5.X 4,83MW
Manufacturer | Nordex
Hub Height | 105 | 120 | 125 | 164
Power
Rated Power | 4830
Peak Power | 4830
Power Regulation Type | Pitch
Voltage | 750
Rotor
Rotor diameter | 149
Number of blades | 3
Rated RPM | 20.5
Rotor tilt | 6
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 26
Restart Wind Speed | 25.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 50
High Temperature Restart | 40
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | S
Values
Certification | IEC 3rd Edition
Vave | 7.5-9.5
Vref | 42
Design TI | 0.11

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 2 | 4 | 5 | 8 | 10 | 12 | 13 | 16 | 18 | 20 | 23 | 24 | 26 | 29 | 31 | 33 | 34
| 3.5 | 66 | 70 | 73 | 77 | 80 | 84 | 87 | 91 | 95 | 98 | 102 | 105 | 109 | 113 | 116 | 120 | 123
| 4 | 155 | 161 | 167 | 173 | 179 | 185 | 191 | 197 | 203 | 209 | 215 | 221 | 227 | 233 | 239 | 246 | 252
| 4.5 | 264 | 273 | 283 | 292 | 301 | 310 | 319 | 328 | 337 | 346 | 355 | 364 | 374 | 383 | 392 | 401 | 410
| 5 | 396 | 409 | 421 | 434 | 447 | 460 | 472 | 485 | 498 | 510 | 523 | 536 | 549 | 561 | 574 | 587 | 600
| 5.5 | 552 | 569 | 586 | 603 | 620 | 637 | 654 | 671 | 688 | 705 | 722 | 739 | 756 | 773 | 790 | 807 | 824
| 6 | 736 | 758 | 780 | 802 | 825 | 847 | 869 | 891 | 913 | 935 | 957 | 979 | 1001 | 1023 | 1046 | 1068 | 1090
| 6.5 | 952 | 980 | 1008 | 1036 | 1064 | 1093 | 1121 | 1149 | 1177 | 1205 | 1233 | 1261 | 1289 | 1317 | 1345 | 1373 | 1401
| 7 | 1204 | 1239 | 1274 | 1309 | 1344 | 1379 | 1414 | 1449 | 1484 | 1519 | 1554 | 1589 | 1624 | 1659 | 1693 | 1728 | 1763
| 7.5 | 1486 | 1529 | 1572 | 1615 | 1657 | 1700 | 1743 | 1785 | 1828 | 1871 | 1913 | 1956 | 1999 | 2041 | 2084 | 2126 | 2169
| 8 | 1780 | 1831 | 1881 | 1932 | 1983 | 2034 | 2084 | 2135 | 2186 | 2236 | 2287 | 2337 | 2388 | 2438 | 2489 | 2539 | 2590
| 8.5 | 2070 | 2129 | 2188 | 2246 | 2305 | 2363 | 2422 | 2481 | 2539 | 2598 | 2656 | 2714 | 2773 | 2831 | 2889 | 2948 | 3006
| 9 | 2349 | 2415 | 2481 | 2548 | 2614 | 2680 | 2746 | 2812 | 2878 | 2944 | 3010 | 3076 | 3142 | 3208 | 3274 | 3339 | 3405
| 9.5 | 2611 | 2685 | 2758 | 2831 | 2905 | 2978 | 3051 | 3124 | 3197 | 3270 | 3344 | 3416 | 3489 | 3562 | 3635 | 3708 | 3782
| 10 | 2860 | 2940 | 3020 | 3100 | 3180 | 3260 | 3340 | 3420 | 3499 | 3579 | 3658 | 3739 | 3819 | 3898 | 3974 | 4049 | 4124
| 10.5 | 3098 | 3185 | 3271 | 3358 | 3444 | 3531 | 3617 | 3703 | 3789 | 3876 | 3963 | 4043 | 4123 | 4199 | 4261 | 4322 | 4384
| 11 | 3330 | 3423 | 3515 | 3608 | 3701 | 3793 | 3886 | 3979 | 4068 | 4151 | 4234 | 4300 | 4365 | 4427 | 4476 | 4525 | 4574
| 11.5 | 3556 | 3655 | 3753 | 3852 | 3951 | 4050 | 4141 | 4228 | 4305 | 4374 | 4442 | 4494 | 4546 | 4596 | 4633 | 4669 | 4706
| 12 | 3777 | 3882 | 3987 | 4092 | 4186 | 4276 | 4353 | 4425 | 4488 | 4544 | 4599 | 4638 | 4677 | 4714 | 4739 | 4763 | 4788
| 12.5 | 3995 | 4105 | 4207 | 4300 | 4380 | 4455 | 4518 | 4576 | 4626 | 4668 | 4710 | 4737 | 4764 | 4789 | 4802 | 4814 | 4827
| 13 | 4205 | 4301 | 4388 | 4466 | 4533 | 4594 | 4643 | 4688 | 4725 | 4754 | 4784 | 4798 | 4813 | 4826 | 4828 | 4829 | 4830
| 13.5 | 4378 | 4459 | 4532 | 4596 | 4649 | 4696 | 4732 | 4764 | 4789 | 4806 | 4823 | 4826 | 4829 | 4830 | 4830 | 4830 | 4830
| 14 | 4518 | 4585 | 4644 | 4694 | 4733 | 4767 | 4791 | 4810 | 4822 | 4827 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830
| 14.5 | 4628 | 4681 | 4726 | 4763 | 4790 | 4811 | 4822 | 4828 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830
| 15 | 4712 | 4751 | 4783 | 4807 | 4820 | 4829 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830
| 15.5 | 4771 | 4798 | 4816 | 4827 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830
| 16 | 4809 | 4823 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830
| 16.5 | 4828 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830
| 17 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830
| 17.5 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830
| 18 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830
| 18.5 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830
| 19 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830
| 19.5 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830
| 20 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830
| 20.5 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830
| 21 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830
| 21.5 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830
| 22 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830
| 22.5 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830
| 23 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830
| 23.5 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830
| 24 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830
| 24.5 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830
| 25 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830 | 4830
| 25.5 | 4821 | 4821 | 4821 | 4821 | 4821 | 4821 | 4821 | 4821 | 4821 | 4821 | 4821 | 4821 | 4821 | 4821 | 4821 | 4821 | 4821
| 26 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782 | 4782

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986
| 3.5 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292
| 4 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597
| 4.5 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972
| 5 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417
| 5.5 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069
| 6 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861
| 6.5 | 0.54583 | 0.54583 | 0.54583 | 0.54583 | 0.54583 | 0.54583 | 0.54583 | 0.54583 | 0.54583 | 0.54583 | 0.54583 | 0.54583 | 0.54583 | 0.54583 | 0.54583 | 0.54583 | 0.54583
| 7 | 0.53403 | 0.53403 | 0.53403 | 0.53403 | 0.53403 | 0.53403 | 0.53403 | 0.53403 | 0.53403 | 0.53403 | 0.53403 | 0.53403 | 0.53403 | 0.53403 | 0.53403 | 0.53403 | 0.53403
| 7.5 | 0.51389 | 0.51389 | 0.51389 | 0.51389 | 0.51389 | 0.51389 | 0.51389 | 0.51389 | 0.51389 | 0.51389 | 0.51389 | 0.51389 | 0.51389 | 0.51389 | 0.51389 | 0.51389 | 0.51389
| 8 | 0.48958 | 0.48958 | 0.48958 | 0.48958 | 0.48958 | 0.48958 | 0.48958 | 0.48958 | 0.48958 | 0.48958 | 0.48958 | 0.48958 | 0.48958 | 0.48958 | 0.48958 | 0.48958 | 0.48958
| 8.5 | 0.46181 | 0.46181 | 0.46181 | 0.46181 | 0.46181 | 0.46181 | 0.46181 | 0.46181 | 0.46181 | 0.46181 | 0.46181 | 0.46181 | 0.46181 | 0.46181 | 0.46181 | 0.46181 | 0.46181
| 9 | 0.43194 | 0.43194 | 0.43194 | 0.43194 | 0.43194 | 0.43194 | 0.43194 | 0.43194 | 0.43194 | 0.43194 | 0.43194 | 0.43194 | 0.43194 | 0.43194 | 0.43194 | 0.43194 | 0.43194
| 9.5 | 0.40208 | 0.40208 | 0.40208 | 0.40208 | 0.40208 | 0.40208 | 0.40208 | 0.40208 | 0.40208 | 0.40208 | 0.40208 | 0.40208 | 0.40208 | 0.40208 | 0.40139 | 0.40069 | 0.4
| 10 | 0.37222 | 0.37222 | 0.37222 | 0.37222 | 0.37222 | 0.37222 | 0.37222 | 0.37222 | 0.37222 | 0.37222 | 0.37153 | 0.37153 | 0.37014 | 0.36944 | 0.36875 | 0.36736 | 0.36597
| 10.5 | 0.34236 | 0.34236 | 0.34236 | 0.34236 | 0.34236 | 0.34236 | 0.34236 | 0.34236 | 0.34167 | 0.34097 | 0.33958 | 0.33889 | 0.3375 | 0.33611 | 0.33472 | 0.33333 | 0.33125
| 11 | 0.31389 | 0.31389 | 0.31389 | 0.31389 | 0.31389 | 0.31319 | 0.31319 | 0.31181 | 0.31111 | 0.30972 | 0.30833 | 0.30694 | 0.30556 | 0.30347 | 0.30208 | 0.3 | 0.29792
| 11.5 | 0.28889 | 0.28889 | 0.28819 | 0.28819 | 0.2875 | 0.28611 | 0.28542 | 0.28403 | 0.28264 | 0.28125 | 0.27986 | 0.27778 | 0.27569 | 0.27431 | 0.27222 | 0.27014 | 0.26806
| 12 | 0.26597 | 0.26597 | 0.26528 | 0.26389 | 0.26319 | 0.26181 | 0.26042 | 0.25903 | 0.25764 | 0.25556 | 0.25347 | 0.25208 | 0.25 | 0.24792 | 0.24583 | 0.24306 | 0.24097
| 12.5 | 0.24514 | 0.24444 | 0.24375 | 0.24236 | 0.24097 | 0.23958 | 0.23819 | 0.23611 | 0.23472 | 0.23264 | 0.23056 | 0.22847 | 0.22639 | 0.22431 | 0.22153 | 0.21944 | 0.21667
| 13 | 0.22639 | 0.22569 | 0.22431 | 0.22292 | 0.22083 | 0.21944 | 0.21736 | 0.21528 | 0.21389 | 0.21181 | 0.20903 | 0.20764 | 0.20486 | 0.20278 | 0.20069 | 0.19792 | 0.19514
| 13.5 | 0.20903 | 0.20764 | 0.20625 | 0.20417 | 0.20278 | 0.20069 | 0.19931 | 0.19722 | 0.19514 | 0.19236 | 0.19028 | 0.18819 | 0.18542 | 0.18333 | 0.18125 | 0.17847 | 0.17569
| 14 | 0.19306 | 0.19167 | 0.18958 | 0.18819 | 0.18611 | 0.18403 | 0.18194 | 0.17986 | 0.17778 | 0.17569 | 0.17292 | 0.17083 | 0.16875 | 0.16597 | 0.16389 | 0.16111 | 0.15833
| 14.5 | 0.17847 | 0.17639 | 0.175 | 0.17292 | 0.17083 | 0.16875 | 0.16667 | 0.16458 | 0.1625 | 0.15972 | 0.15764 | 0.15556 | 0.15278 | 0.15 | 0.14792 | 0.14514 | 0.14306
| 15 | 0.16528 | 0.16319 | 0.16111 | 0.15903 | 0.15694 | 0.15486 | 0.15278 | 0.15069 | 0.14792 | 0.14583 | 0.14375 | 0.14097 | 0.13889 | 0.13611 | 0.13403 | 0.13125 | 0.12847
| 15.5 | 0.15278 | 0.15069 | 0.14861 | 0.14653 | 0.14444 | 0.14236 | 0.14028 | 0.1375 | 0.13542 | 0.13333 | 0.13056 | 0.12847 | 0.12569 | 0.12292 | 0.12083 | 0.11806 | 0.11597
| 16 | 0.14097 | 0.13958 | 0.1375 | 0.13472 | 0.13264 | 0.13056 | 0.12847 | 0.12569 | 0.12361 | 0.12153 | 0.11875 | 0.11667 | 0.11389 | 0.11181 | 0.10972 | 0.10694 | 0.10486
| 16.5 | 0.13056 | 0.12847 | 0.12639 | 0.12431 | 0.12222 | 0.12014 | 0.11806 | 0.11528 | 0.11319 | 0.11042 | 0.10833 | 0.10625 | 0.10347 | 0.10139 | 0.099306 | 0.097917 | 0.095833
| 17 | 0.12153 | 0.11944 | 0.11667 | 0.11458 | 0.1125 | 0.11042 | 0.10764 | 0.10556 | 0.10347 | 0.10069 | 0.098611 | 0.096528 | 0.094444 | 0.093056 | 0.090972 | 0.088889 | 0.0875
| 17.5 | 0.1125 | 0.11042 | 0.10833 | 0.10556 | 0.10347 | 0.10139 | 0.099306 | 0.096528 | 0.094444 | 0.092361 | 0.090278 | 0.088194 | 0.086806 | 0.084722 | 0.083333 | 0.081944 | 0.080556
| 18 | 0.10417 | 0.10208 | 0.1 | 0.097917 | 0.095833 | 0.093056 | 0.090972 | 0.088889 | 0.086806 | 0.084722 | 0.083333 | 0.08125 | 0.079861 | 0.078472 | 0.077083 | 0.075694 | 0.074306
| 18.5 | 0.097222 | 0.095139 | 0.093056 | 0.090278 | 0.088194 | 0.086111 | 0.084028 | 0.081944 | 0.080556 | 0.078472 | 0.077083 | 0.075694 | 0.073611 | 0.072222 | 0.070833 | 0.070139 | 0.099
| 19 | 0.090972 | 0.088194 | 0.086111 | 0.084028 | 0.081944 | 0.079861 | 0.078472 | 0.076389 | 0.075 | 0.072917 | 0.071528 | 0.070139 | 0.099 | 0.097 | 0.095 | 0.094 | 0.092
| 19.5 | 0.084722 | 0.082639 | 0.080556 | 0.078472 | 0.076389 | 0.075 | 0.072917 | 0.071528 | 0.070139 | 0.099 | 0.097 | 0.095 | 0.093 | 0.091 | 0.089 | 0.088 | 0.086
| 20 | 0.079861 | 0.077778 | 0.075694 | 0.073611 | 0.072222 | 0.070139 | 0.099 | 0.097 | 0.095 | 0.093 | 0.091 | 0.089 | 0.087 | 0.086 | 0.084 | 0.083 | 0.081
| 20.5 | 0.075 | 0.073611 | 0.071528 | 0.069444 | 0.098 | 0.096 | 0.094 | 0.092 | 0.09 | 0.088 | 0.086 | 0.084 | 0.083 | 0.081 | 0.08 | 0.078 | 0.077
| 21 | 0.071528 | 0.069444 | 0.098 | 0.095 | 0.093 | 0.091 | 0.089 | 0.087 | 0.085 | 0.083 | 0.082 | 0.08 | 0.079 | 0.077 | 0.076 | 0.074 | 0.073
| 21.5 | 0.098 | 0.096 | 0.093 | 0.091 | 0.089 | 0.087 | 0.085 | 0.083 | 0.081 | 0.08 | 0.078 | 0.077 | 0.075 | 0.074 | 0.072 | 0.071 | 0.07
| 22 | 0.094 | 0.091 | 0.089 | 0.087 | 0.085 | 0.083 | 0.081 | 0.08 | 0.078 | 0.076 | 0.075 | 0.073 | 0.072 | 0.071 | 0.069 | 0.068 | 0.067
| 22.5 | 0.087 | 0.084 | 0.083 | 0.081 | 0.079 | 0.077 | 0.075 | 0.074 | 0.072 | 0.07 | 0.07 | 0.068 | 0.067 | 0.066 | 0.064 | 0.063 | 0.062
| 23 | 0.081 | 0.078 | 0.076 | 0.075 | 0.073 | 0.071 | 0.069 | 0.069 | 0.067 | 0.065 | 0.064 | 0.063 | 0.062 | 0.061 | 0.059 | 0.058 | 0.057
| 23.5 | 0.074 | 0.072 | 0.07 | 0.069 | 0.067 | 0.066 | 0.064 | 0.063 | 0.062 | 0.06 | 0.059 | 0.058 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053
| 24 | 0.069 | 0.067 | 0.065 | 0.064 | 0.062 | 0.061 | 0.059 | 0.059 | 0.057 | 0.056 | 0.055 | 0.053 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049
| 24.5 | 0.063 | 0.061 | 0.06 | 0.059 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053 | 0.051 | 0.051 | 0.049 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045
| 25 | 0.059 | 0.057 | 0.056 | 0.055 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.045 | 0.043 | 0.043 | 0.042
| 25.5 | 0.054 | 0.053 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039
| 26 | 0.051 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.038 | 0.037 | 0.037 | 0.036