## Sheet1
PROPERTIES
General
Name | Nordex N149/5.X 4,72MW
Manufacturer | Nordex
Hub Height | 105 | 120 | 125 | 164
Power
Rated Power | 4720
Peak Power | 4720
Power Regulation Type | Pitch
Voltage | 750
Rotor
Rotor diameter | 149
Number of blades | 3
Rated RPM | 20.5
Rotor tilt | 6
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 26
Restart Wind Speed | 25.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 50
High Temperature Restart | 40
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | S
Values
Certification | IEC 3rd Edition
Vave | 7.5-9.5
Vref | 42
Design TI | 0.11

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 2 | 4 | 5 | 8 | 10 | 12 | 13 | 16 | 18 | 20 | 23 | 24 | 26 | 29 | 31 | 33 | 34
| 3.5 | 66 | 70 | 73 | 77 | 80 | 84 | 87 | 91 | 95 | 98 | 102 | 105 | 109 | 113 | 116 | 120 | 123
| 4 | 155 | 161 | 167 | 173 | 179 | 185 | 191 | 197 | 203 | 209 | 215 | 221 | 227 | 233 | 239 | 246 | 252
| 4.5 | 264 | 273 | 283 | 292 | 301 | 310 | 319 | 328 | 337 | 346 | 355 | 364 | 374 | 383 | 392 | 401 | 410
| 5 | 396 | 409 | 421 | 434 | 447 | 460 | 472 | 485 | 498 | 510 | 523 | 536 | 549 | 561 | 574 | 587 | 600
| 5.5 | 552 | 569 | 586 | 603 | 620 | 637 | 654 | 671 | 688 | 705 | 722 | 739 | 756 | 773 | 790 | 807 | 824
| 6 | 736 | 758 | 780 | 802 | 825 | 847 | 869 | 891 | 913 | 935 | 957 | 979 | 1001 | 1023 | 1045 | 1068 | 1090
| 6.5 | 952 | 980 | 1008 | 1036 | 1065 | 1093 | 1121 | 1149 | 1177 | 1205 | 1233 | 1261 | 1289 | 1317 | 1345 | 1373 | 1401
| 7 | 1203 | 1238 | 1273 | 1308 | 1343 | 1378 | 1413 | 1448 | 1483 | 1518 | 1553 | 1588 | 1622 | 1657 | 1692 | 1727 | 1762
| 7.5 | 1479 | 1521 | 1564 | 1606 | 1649 | 1691 | 1734 | 1776 | 1819 | 1861 | 1904 | 1946 | 1988 | 2031 | 2073 | 2115 | 2158
| 8 | 1759 | 1809 | 1860 | 1910 | 1960 | 2010 | 2060 | 2110 | 2160 | 2210 | 2260 | 2310 | 2360 | 2410 | 2460 | 2510 | 2560
| 8.5 | 2033 | 2091 | 2148 | 2206 | 2264 | 2321 | 2379 | 2436 | 2494 | 2551 | 2609 | 2666 | 2724 | 2781 | 2838 | 2896 | 2953
| 9 | 2293 | 2358 | 2423 | 2488 | 2552 | 2617 | 2682 | 2746 | 2811 | 2875 | 2940 | 3004 | 3069 | 3133 | 3197 | 3262 | 3326
| 9.5 | 2538 | 2609 | 2681 | 2752 | 2823 | 2895 | 2966 | 3037 | 3108 | 3179 | 3250 | 3321 | 3392 | 3463 | 3534 | 3605 | 3676
| 10 | 2771 | 2848 | 2926 | 3004 | 3081 | 3159 | 3236 | 3314 | 3391 | 3468 | 3545 | 3623 | 3701 | 3778 | 3854 | 3927 | 4000
| 10.5 | 2995 | 3079 | 3163 | 3246 | 3330 | 3414 | 3497 | 3581 | 3664 | 3748 | 3832 | 3914 | 3991 | 4068 | 4136 | 4196 | 4256
| 11 | 3214 | 3303 | 3393 | 3483 | 3572 | 3662 | 3751 | 3841 | 3931 | 4013 | 4094 | 4169 | 4232 | 4295 | 4350 | 4397 | 4445
| 11.5 | 3428 | 3523 | 3619 | 3714 | 3809 | 3905 | 4000 | 4084 | 4168 | 4237 | 4303 | 4364 | 4414 | 4465 | 4508 | 4543 | 4578
| 12 | 3637 | 3739 | 3840 | 3941 | 4041 | 4128 | 4214 | 4283 | 4353 | 4409 | 4462 | 4510 | 4548 | 4586 | 4617 | 4641 | 4665
| 12.5 | 3844 | 3950 | 4056 | 4149 | 4238 | 4310 | 4382 | 4438 | 4494 | 4537 | 4578 | 4613 | 4640 | 4666 | 4685 | 4697 | 4709
| 13 | 4046 | 4148 | 4241 | 4319 | 4394 | 4452 | 4511 | 4554 | 4597 | 4628 | 4656 | 4680 | 4694 | 4709 | 4717 | 4718 | 4720
| 13.5 | 4223 | 4311 | 4389 | 4453 | 4514 | 4560 | 4605 | 4636 | 4667 | 4686 | 4702 | 4714 | 4717 | 4720 | 4720 | 4720 | 4720
| 14 | 4367 | 4441 | 4505 | 4556 | 4604 | 4637 | 4670 | 4688 | 4707 | 4714 | 4718 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720
| 14.5 | 4483 | 4543 | 4594 | 4632 | 4667 | 4688 | 4708 | 4714 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720
| 15 | 4573 | 4619 | 4657 | 4682 | 4705 | 4713 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720
| 15.5 | 4639 | 4672 | 4697 | 4710 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720
| 16 | 4684 | 4705 | 4717 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720
| 16.5 | 4710 | 4719 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720
| 17 | 4719 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720
| 17.5 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720
| 18 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720
| 18.5 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720
| 19 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720
| 19.5 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720
| 20 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720
| 20.5 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720
| 21 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720
| 21.5 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720
| 22 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720
| 22.5 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720
| 23 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720
| 23.5 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720
| 24 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720
| 24.5 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720
| 25 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720
| 25.5 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720
| 26 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720 | 4720

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986 | 0.57986
| 3.5 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292 | 0.57292
| 4 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597 | 0.56597
| 4.5 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972
| 5 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417
| 5.5 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069 | 0.55069
| 6 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861
| 6.5 | 0.54306 | 0.54306 | 0.54306 | 0.54306 | 0.54306 | 0.54306 | 0.54306 | 0.54306 | 0.54306 | 0.54306 | 0.54306 | 0.54306 | 0.54306 | 0.54306 | 0.54306 | 0.54306 | 0.54306
| 7 | 0.52778 | 0.52778 | 0.52778 | 0.52778 | 0.52778 | 0.52778 | 0.52778 | 0.52778 | 0.52778 | 0.52778 | 0.52778 | 0.52778 | 0.52778 | 0.52778 | 0.52778 | 0.52778 | 0.52778
| 7.5 | 0.50556 | 0.50556 | 0.50556 | 0.50556 | 0.50556 | 0.50556 | 0.50556 | 0.50556 | 0.50556 | 0.50556 | 0.50556 | 0.50556 | 0.50556 | 0.50556 | 0.50556 | 0.50556 | 0.50556
| 8 | 0.47847 | 0.47847 | 0.47847 | 0.47847 | 0.47847 | 0.47847 | 0.47847 | 0.47847 | 0.47847 | 0.47847 | 0.47847 | 0.47847 | 0.47847 | 0.47847 | 0.47847 | 0.47847 | 0.47847
| 8.5 | 0.44931 | 0.44931 | 0.44931 | 0.44931 | 0.44931 | 0.44931 | 0.44931 | 0.44931 | 0.44931 | 0.44931 | 0.44931 | 0.44931 | 0.44931 | 0.44931 | 0.44931 | 0.44931 | 0.44931
| 9 | 0.41944 | 0.41944 | 0.41944 | 0.41944 | 0.41944 | 0.41944 | 0.41944 | 0.41944 | 0.41944 | 0.41944 | 0.41944 | 0.41944 | 0.41944 | 0.41944 | 0.41944 | 0.41944 | 0.41875
| 9.5 | 0.38819 | 0.38819 | 0.38819 | 0.38819 | 0.38819 | 0.38819 | 0.38819 | 0.38819 | 0.38819 | 0.38819 | 0.38819 | 0.38819 | 0.38819 | 0.38819 | 0.38819 | 0.3875 | 0.38681
| 10 | 0.35764 | 0.35764 | 0.35764 | 0.35764 | 0.35764 | 0.35764 | 0.35764 | 0.35764 | 0.35764 | 0.35764 | 0.35764 | 0.35694 | 0.35694 | 0.35556 | 0.35486 | 0.35417 | 0.35278
| 10.5 | 0.32778 | 0.32778 | 0.32778 | 0.32778 | 0.32778 | 0.32778 | 0.32778 | 0.32778 | 0.32708 | 0.32708 | 0.32639 | 0.325 | 0.32431 | 0.32292 | 0.32153 | 0.32014 | 0.31875
| 11 | 0.30069 | 0.30069 | 0.30069 | 0.30069 | 0.30069 | 0.3 | 0.3 | 0.29931 | 0.29792 | 0.29722 | 0.29583 | 0.29514 | 0.29375 | 0.29167 | 0.29028 | 0.28889 | 0.28681
| 11.5 | 0.27639 | 0.27639 | 0.27639 | 0.27569 | 0.27569 | 0.275 | 0.27361 | 0.27292 | 0.27153 | 0.27014 | 0.26875 | 0.26736 | 0.26597 | 0.26389 | 0.26181 | 0.26042 | 0.25833
| 12 | 0.25486 | 0.25486 | 0.25417 | 0.25347 | 0.25278 | 0.25139 | 0.25 | 0.24931 | 0.24722 | 0.24583 | 0.24444 | 0.24236 | 0.24097 | 0.23889 | 0.23681 | 0.23472 | 0.23264
| 12.5 | 0.23542 | 0.23472 | 0.23403 | 0.23264 | 0.23194 | 0.23056 | 0.22917 | 0.22708 | 0.22569 | 0.22431 | 0.22222 | 0.22014 | 0.21806 | 0.21597 | 0.21389 | 0.21181 | 0.20972
| 13 | 0.21736 | 0.21667 | 0.21528 | 0.21389 | 0.2125 | 0.21111 | 0.20972 | 0.20764 | 0.20556 | 0.20417 | 0.20208 | 0.2 | 0.19792 | 0.19583 | 0.19375 | 0.19167 | 0.18889
| 13.5 | 0.20069 | 0.2 | 0.19861 | 0.19722 | 0.19514 | 0.19375 | 0.19167 | 0.19028 | 0.18819 | 0.18611 | 0.18403 | 0.18194 | 0.17986 | 0.17708 | 0.175 | 0.17292 | 0.17083
| 14 | 0.18542 | 0.18403 | 0.18264 | 0.18125 | 0.17917 | 0.17778 | 0.17569 | 0.17361 | 0.17153 | 0.16944 | 0.16736 | 0.16528 | 0.16319 | 0.16111 | 0.15833 | 0.15625 | 0.15417
| 14.5 | 0.17153 | 0.17014 | 0.16875 | 0.16667 | 0.16528 | 0.16319 | 0.16111 | 0.15903 | 0.15694 | 0.15486 | 0.15278 | 0.15069 | 0.14861 | 0.14583 | 0.14375 | 0.14167 | 0.13889
| 15 | 0.15903 | 0.15764 | 0.15556 | 0.15417 | 0.15208 | 0.15 | 0.14792 | 0.14583 | 0.14375 | 0.14167 | 0.13889 | 0.13681 | 0.13472 | 0.13264 | 0.12986 | 0.12778 | 0.125
| 15.5 | 0.14722 | 0.14583 | 0.14375 | 0.14167 | 0.13958 | 0.1375 | 0.13542 | 0.13333 | 0.13125 | 0.12917 | 0.12708 | 0.125 | 0.12222 | 0.12014 | 0.11806 | 0.11528 | 0.11319
| 16 | 0.13681 | 0.13472 | 0.13264 | 0.13056 | 0.12847 | 0.12708 | 0.12431 | 0.12222 | 0.12014 | 0.11806 | 0.11597 | 0.11319 | 0.11111 | 0.10903 | 0.10694 | 0.10486 | 0.10278
| 16.5 | 0.12639 | 0.125 | 0.12292 | 0.12083 | 0.11875 | 0.11667 | 0.11458 | 0.1125 | 0.10972 | 0.10764 | 0.10556 | 0.10347 | 0.10139 | 0.099306 | 0.097222 | 0.095139 | 0.09375
| 17 | 0.11736 | 0.11528 | 0.11319 | 0.11181 | 0.10903 | 0.10764 | 0.10486 | 0.10278 | 0.10069 | 0.098611 | 0.096528 | 0.094444 | 0.092361 | 0.090278 | 0.088889 | 0.086806 | 0.085417
| 17.5 | 0.10903 | 0.10694 | 0.10486 | 0.10278 | 0.10069 | 0.098611 | 0.096528 | 0.094444 | 0.092361 | 0.090278 | 0.088194 | 0.086111 | 0.084722 | 0.082639 | 0.08125 | 0.079861 | 0.078472
| 18 | 0.10139 | 0.099306 | 0.097222 | 0.095139 | 0.093056 | 0.090972 | 0.088889 | 0.086806 | 0.084722 | 0.082639 | 0.08125 | 0.079861 | 0.077778 | 0.076389 | 0.075 | 0.073611 | 0.072222
| 18.5 | 0.094444 | 0.092361 | 0.090278 | 0.088194 | 0.086111 | 0.084028 | 0.081944 | 0.080556 | 0.078472 | 0.077083 | 0.075 | 0.073611 | 0.072222 | 0.070833 | 0.069444 | 0.098 | 0.096
| 19 | 0.088194 | 0.086111 | 0.084028 | 0.081944 | 0.079861 | 0.078472 | 0.076389 | 0.075 | 0.072917 | 0.071528 | 0.070139 | 0.099 | 0.097 | 0.095 | 0.093 | 0.092 | 0.09
| 19.5 | 0.082639 | 0.080556 | 0.078472 | 0.077083 | 0.075 | 0.072917 | 0.071528 | 0.070139 | 0.098 | 0.096 | 0.094 | 0.092 | 0.091 | 0.089 | 0.087 | 0.086 | 0.084
| 20 | 0.077778 | 0.075694 | 0.073611 | 0.072222 | 0.070139 | 0.099 | 0.097 | 0.095 | 0.093 | 0.091 | 0.089 | 0.087 | 0.085 | 0.084 | 0.082 | 0.081 | 0.079
| 20.5 | 0.073611 | 0.071528 | 0.070139 | 0.098 | 0.096 | 0.093 | 0.091 | 0.089 | 0.087 | 0.086 | 0.084 | 0.082 | 0.081 | 0.079 | 0.078 | 0.076 | 0.075
| 21 | 0.069444 | 0.098 | 0.095 | 0.093 | 0.091 | 0.089 | 0.087 | 0.085 | 0.083 | 0.081 | 0.08 | 0.078 | 0.077 | 0.075 | 0.074 | 0.073 | 0.071
| 21.5 | 0.096 | 0.093 | 0.091 | 0.089 | 0.087 | 0.085 | 0.083 | 0.081 | 0.079 | 0.078 | 0.076 | 0.075 | 0.073 | 0.072 | 0.071 | 0.069 | 0.068
| 22 | 0.092 | 0.089 | 0.087 | 0.085 | 0.083 | 0.081 | 0.079 | 0.078 | 0.076 | 0.075 | 0.073 | 0.072 | 0.07 | 0.069 | 0.068 | 0.067 | 0.066
| 22.5 | 0.085 | 0.083 | 0.081 | 0.079 | 0.077 | 0.075 | 0.073 | 0.072 | 0.07 | 0.07 | 0.068 | 0.067 | 0.065 | 0.064 | 0.063 | 0.062 | 0.061
| 23 | 0.079 | 0.076 | 0.075 | 0.073 | 0.071 | 0.069 | 0.068 | 0.067 | 0.065 | 0.064 | 0.063 | 0.062 | 0.06 | 0.059 | 0.058 | 0.057 | 0.057
| 23.5 | 0.073 | 0.07 | 0.069 | 0.067 | 0.066 | 0.064 | 0.062 | 0.062 | 0.06 | 0.059 | 0.058 | 0.057 | 0.055 | 0.055 | 0.054 | 0.053 | 0.052
| 24 | 0.067 | 0.065 | 0.064 | 0.062 | 0.061 | 0.059 | 0.058 | 0.057 | 0.056 | 0.055 | 0.053 | 0.053 | 0.051 | 0.051 | 0.05 | 0.049 | 0.048
| 24.5 | 0.062 | 0.06 | 0.059 | 0.057 | 0.056 | 0.055 | 0.053 | 0.053 | 0.051 | 0.051 | 0.049 | 0.049 | 0.047 | 0.047 | 0.046 | 0.045 | 0.045
| 25 | 0.058 | 0.056 | 0.055 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.043 | 0.042 | 0.041
| 25.5 | 0.053 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.042 | 0.04 | 0.04 | 0.039 | 0.039 | 0.038
| 26 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.038 | 0.037 | 0.037 | 0.036 | 0.036