## Sheet1
PROPERTIES
General
Name | Nordex N155/5.X Class B 5,7MW
Manufacturer | Nordex
Hub Height | 108 | 120
Power
Rated Power | 5700
Peak Power | 5700
Power Regulation Type | Pitch
Voltage | 750
Rotor
Rotor diameter | 155
Number of blades | 3
Rated RPM | 10.36
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 25
Restart Wind Speed | 24
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20.5
Low Temperature Restart | -19.5
High Temperature Shutdown | 45
High Temperature Restart | 40
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | B
Values
Certification | IEC 3rd Edition
Vave | 8.5
Vref | 42.5
Design TI | 0.16

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 24 | 25 | 26 | 28 | 32 | 36 | 40 | 44 | 48 | 52 | 56
| 3.5 | 106 | 111 | 116 | 121 | 127 | 133 | 139 | 144 | 150 | 156 | 161
| 4 | 214 | 222 | 229 | 236 | 244 | 252 | 261 | 269 | 277 | 285 | 292
| 4.5 | 347 | 357 | 367 | 376 | 388 | 399 | 410 | 421 | 432 | 443 | 454
| 5 | 507 | 520 | 533 | 546 | 561 | 576 | 591 | 605 | 620 | 634 | 648
| 5.5 | 696 | 713 | 731 | 748 | 768 | 788 | 808 | 827 | 846 | 865 | 884
| 6 | 924 | 947 | 970 | 993 | 1018 | 1043 | 1069 | 1093 | 1118 | 1142 | 1166
| 6.5 | 1192 | 1221 | 1250 | 1279 | 1311 | 1343 | 1375 | 1406 | 1437 | 1467 | 1497
| 7 | 1504 | 1540 | 1576 | 1612 | 1652 | 1692 | 1732 | 1771 | 1809 | 1847 | 1884
| 7.5 | 1863 | 1908 | 1953 | 1998 | 2046 | 2093 | 2141 | 2187 | 2234 | 2279 | 2324
| 8 | 2268 | 2321 | 2375 | 2428 | 2485 | 2541 | 2597 | 2652 | 2706 | 2759 | 2812
| 8.5 | 2715 | 2778 | 2841 | 2903 | 2969 | 3035 | 3101 | 3164 | 3228 | 3289 | 3351
| 9 | 3207 | 3280 | 3353 | 3425 | 3497 | 3569 | 3641 | 3710 | 3779 | 3847 | 3914
| 9.5 | 3714 | 3797 | 3880 | 3963 | 4037 | 4110 | 4184 | 4255 | 4326 | 4394 | 4463
| 10 | 4209 | 4301 | 4393 | 4485 | 4550 | 4614 | 4679 | 4741 | 4803 | 4864 | 4924
| 10.5 | 4633 | 4729 | 4825 | 4921 | 4970 | 5019 | 5068 | 5115 | 5162 | 5205 | 5247
| 11 | 4975 | 5062 | 5149 | 5236 | 5266 | 5296 | 5326 | 5355 | 5384 | 5408 | 5432
| 11.5 | 5209 | 5279 | 5350 | 5420 | 5438 | 5456 | 5475 | 5492 | 5510 | 5526 | 5542
| 12 | 5370 | 5422 | 5474 | 5527 | 5543 | 5560 | 5577 | 5593 | 5609 | 5620 | 5631
| 12.5 | 5505 | 5543 | 5582 | 5621 | 5630 | 5640 | 5649 | 5658 | 5667 | 5673 | 5679
| 13 | 5586 | 5614 | 5643 | 5672 | 5677 | 5683 | 5688 | 5693 | 5699 | 5699 | 5700
| 13.5 | 5650 | 5667 | 5683 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700
| 14 | 5680 | 5687 | 5693 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700
| 14.5 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700
| 15 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700
| 15.5 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700
| 16 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700
| 16.5 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700
| 17 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700
| 17.5 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700
| 18 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700
| 18.5 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700
| 19 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700
| 19.5 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700
| 20 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700
| 20.5 | 5580 | 5580 | 5580 | 5580 | 5580 | 5580 | 5580 | 5580 | 5580 | 5580 | 5580
| 21 | 5460 | 5460 | 5460 | 5460 | 5460 | 5460 | 5460 | 5460 | 5460 | 5460 | 5460
| 21.5 | 5340 | 5340 | 5340 | 5340 | 5340 | 5340 | 5340 | 5340 | 5340 | 5340 | 5340
| 22 | 5220 | 5220 | 5220 | 5220 | 5220 | 5220 | 5220 | 5220 | 5220 | 5220 | 5220
| 22.5 | 5100 | 5100 | 5100 | 5100 | 5100 | 5100 | 5100 | 5100 | 5100 | 5100 | 5100
| 23 | 4980 | 4980 | 4980 | 4980 | 4980 | 4980 | 4980 | 4980 | 4980 | 4980 | 4980
| 23.5 | 4860 | 4860 | 4860 | 4860 | 4860 | 4860 | 4860 | 4860 | 4860 | 4860 | 4860
| 24 | 4740 | 4740 | 4740 | 4740 | 4740 | 4740 | 4740 | 4740 | 4740 | 4740 | 4740
| 24.5 | 4620 | 4620 | 4620 | 4620 | 4620 | 4620 | 4620 | 4620 | 4620 | 4620 | 4620
| 25 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.884 | 0.884 | 0.884 | 0.884 | 0.884 | 0.885 | 0.885 | 0.885 | 0.885 | 0.885 | 0.886
| 3.5 | 0.835 | 0.837 | 0.84 | 0.842 | 0.844 | 0.847 | 0.849 | 0.851 | 0.854 | 0.856 | 0.858
| 4 | 0.814 | 0.817 | 0.82 | 0.822 | 0.825 | 0.828 | 0.831 | 0.833 | 0.836 | 0.838 | 0.841
| 4.5 | 0.794 | 0.797 | 0.8 | 0.802 | 0.807 | 0.813 | 0.818 | 0.821 | 0.825 | 0.829 | 0.832
| 5 | 0.779 | 0.776 | 0.774 | 0.771 | 0.783 | 0.795 | 0.807 | 0.811 | 0.814 | 0.818 | 0.822
| 5.5 | 0.774 | 0.767 | 0.761 | 0.755 | 0.77 | 0.786 | 0.801 | 0.805 | 0.81 | 0.814 | 0.818
| 6 | 0.768 | 0.762 | 0.756 | 0.75 | 0.766 | 0.782 | 0.799 | 0.803 | 0.808 | 0.812 | 0.816
| 6.5 | 0.771 | 0.765 | 0.76 | 0.754 | 0.77 | 0.786 | 0.801 | 0.806 | 0.81 | 0.814 | 0.818
| 7 | 0.769 | 0.763 | 0.757 | 0.751 | 0.767 | 0.782 | 0.798 | 0.802 | 0.806 | 0.81 | 0.814
| 7.5 | 0.771 | 0.765 | 0.759 | 0.753 | 0.769 | 0.784 | 0.8 | 0.804 | 0.808 | 0.812 | 0.816
| 8 | 0.769 | 0.763 | 0.757 | 0.751 | 0.766 | 0.781 | 0.796 | 0.799 | 0.803 | 0.805 | 0.808
| 8.5 | 0.765 | 0.76 | 0.755 | 0.749 | 0.76 | 0.771 | 0.782 | 0.783 | 0.784 | 0.784 | 0.784
| 9 | 0.747 | 0.742 | 0.737 | 0.732 | 0.738 | 0.744 | 0.749 | 0.748 | 0.747 | 0.746 | 0.744
| 9.5 | 0.716 | 0.712 | 0.707 | 0.703 | 0.704 | 0.705 | 0.706 | 0.703 | 0.7 | 0.696 | 0.692
| 10 | 0.675 | 0.671 | 0.667 | 0.663 | 0.66 | 0.657 | 0.654 | 0.65 | 0.645 | 0.64 | 0.635
| 10.5 | 0.627 | 0.623 | 0.619 | 0.615 | 0.609 | 0.604 | 0.598 | 0.591 | 0.583 | 0.575 | 0.566
| 11 | 0.577 | 0.571 | 0.565 | 0.558 | 0.55 | 0.542 | 0.534 | 0.524 | 0.515 | 0.506 | 0.498
| 11.5 | 0.522 | 0.513 | 0.505 | 0.497 | 0.487 | 0.478 | 0.468 | 0.46 | 0.452 | 0.443 | 0.435
| 12 | 0.466 | 0.457 | 0.448 | 0.439 | 0.431 | 0.422 | 0.414 | 0.406 | 0.398 | 0.39 | 0.383
| 12.5 | 0.414 | 0.405 | 0.397 | 0.388 | 0.38 | 0.372 | 0.364 | 0.357 | 0.35 | 0.343 | 0.336
| 13 | 0.369 | 0.361 | 0.353 | 0.346 | 0.338 | 0.331 | 0.323 | 0.317 | 0.312 | 0.305 | 0.299
| 13.5 | 0.331 | 0.323 | 0.316 | 0.308 | 0.301 | 0.295 | 0.288 | 0.282 | 0.276 | 0.27 | 0.264
| 14 | 0.294 | 0.287 | 0.281 | 0.274 | 0.268 | 0.262 | 0.256 | 0.251 | 0.245 | 0.24 | 0.235
| 14.5 | 0.265 | 0.259 | 0.253 | 0.246 | 0.241 | 0.235 | 0.23 | 0.225 | 0.22 | 0.216 | 0.211
| 15 | 0.238 | 0.232 | 0.227 | 0.221 | 0.216 | 0.211 | 0.206 | 0.202 | 0.198 | 0.194 | 0.19
| 15.5 | 0.214 | 0.21 | 0.205 | 0.2 | 0.195 | 0.191 | 0.187 | 0.183 | 0.179 | 0.176 | 0.172
| 16 | 0.194 | 0.19 | 0.185 | 0.181 | 0.177 | 0.173 | 0.17 | 0.166 | 0.163 | 0.16 | 0.157
| 16.5 | 0.177 | 0.173 | 0.169 | 0.165 | 0.162 | 0.158 | 0.155 | 0.152 | 0.149 | 0.146 | 0.143
| 17 | 0.162 | 0.158 | 0.155 | 0.151 | 0.148 | 0.145 | 0.142 | 0.139 | 0.136 | 0.134 | 0.131
| 17.5 | 0.149 | 0.145 | 0.142 | 0.139 | 0.136 | 0.133 | 0.13 | 0.128 | 0.125 | 0.123 | 0.121
| 18 | 0.137 | 0.134 | 0.131 | 0.128 | 0.125 | 0.123 | 0.12 | 0.118 | 0.115 | 0.113 | 0.111
| 18.5 | 0.126 | 0.124 | 0.121 | 0.118 | 0.116 | 0.113 | 0.111 | 0.109 | 0.107 | 0.105 | 0.103
| 19 | 0.117 | 0.114 | 0.112 | 0.11 | 0.107 | 0.105 | 0.103 | 0.101 | 0.099 | 0.098 | 0.096
| 19.5 | 0.109 | 0.106 | 0.104 | 0.102 | 0.1 | 0.098 | 0.096 | 0.094 | 0.092 | 0.091 | 0.089
| 20 | 0.101 | 0.099 | 0.097 | 0.095 | 0.093 | 0.091 | 0.089 | 0.088 | 0.086 | 0.085 | 0.083
| 20.5 | 0.094 | 0.093 | 0.091 | 0.089 | 0.087 | 0.085 | 0.084 | 0.082 | 0.081 | 0.079 | 0.078
| 21 | 0.088 | 0.087 | 0.085 | 0.083 | 0.081 | 0.08 | 0.078 | 0.077 | 0.076 | 0.074 | 0.073
| 21.5 | 0.083 | 0.081 | 0.08 | 0.078 | 0.076 | 0.075 | 0.074 | 0.072 | 0.071 | 0.07 | 0.069
| 22 | 0.078 | 0.076 | 0.075 | 0.073 | 0.072 | 0.071 | 0.069 | 0.068 | 0.067 | 0.066 | 0.065
| 22.5 | 0.073 | 0.072 | 0.071 | 0.069 | 0.068 | 0.067 | 0.065 | 0.064 | 0.063 | 0.062 | 0.061
| 23 | 0.069 | 0.068 | 0.067 | 0.065 | 0.064 | 0.063 | 0.062 | 0.061 | 0.06 | 0.059 | 0.058
| 23.5 | 0.065 | 0.064 | 0.063 | 0.062 | 0.061 | 0.059 | 0.058 | 0.057 | 0.056 | 0.055 | 0.055
| 24 | 0.062 | 0.061 | 0.06 | 0.058 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053 | 0.053 | 0.052
| 24.5 | 0.059 | 0.058 | 0.056 | 0.055 | 0.054 | 0.053 | 0.052 | 0.052 | 0.051 | 0.05 | 0.049
| 25 | 0.056 | 0.055 | 0.054 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.047