## Sheet1
PROPERTIES
General
Name | Nordex N163/5.X Class B 5,7MW
Manufacturer | Nordex
Hub Height | 116 | 120 | 148 | 159 | 164
Power
Rated Power | 5700
Peak Power | 5700
Power Regulation Type | Pitch
Voltage | 750
Rotor
Rotor diameter | 163
Number of blades | 3
Rated RPM | 11.8
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 26
Restart Wind Speed | 25.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 45
High Temperature Restart | 40
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | B
Values
Certification | IEC 3rd Edition
Vave | 6.5-8
Vref | 38.8-40.3
Design TI | 0.16

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 18 | 21 | 23 | 25 | 28 | 30 | 32 | 34 | 37 | 39 | 41 | 44 | 46 | 48 | 50 | 53 | 55
| 3.5 | 97 | 101 | 106 | 110 | 115 | 119 | 124 | 128 | 133 | 137 | 142 | 146 | 151 | 155 | 159 | 164 | 168
| 4 | 202 | 209 | 217 | 224 | 231 | 239 | 246 | 254 | 261 | 268 | 276 | 283 | 290 | 298 | 305 | 312 | 320
| 4.5 | 332 | 343 | 354 | 365 | 376 | 387 | 398 | 409 | 420 | 431 | 441 | 452 | 463 | 474 | 485 | 496 | 507
| 5 | 487 | 502 | 517 | 533 | 548 | 563 | 578 | 594 | 609 | 624 | 639 | 655 | 670 | 685 | 700 | 716 | 731
| 5.5 | 671 | 692 | 712 | 732 | 753 | 773 | 793 | 814 | 834 | 854 | 875 | 895 | 915 | 936 | 956 | 976 | 997
| 6 | 890 | 916 | 943 | 969 | 996 | 1022 | 1048 | 1075 | 1101 | 1127 | 1154 | 1180 | 1206 | 1232 | 1259 | 1285 | 1311
| 6.5 | 1148 | 1181 | 1214 | 1248 | 1281 | 1315 | 1348 | 1382 | 1415 | 1448 | 1482 | 1515 | 1548 | 1582 | 1615 | 1648 | 1682
| 7 | 1447 | 1489 | 1531 | 1572 | 1614 | 1656 | 1697 | 1739 | 1780 | 1822 | 1863 | 1905 | 1946 | 1988 | 2029 | 2071 | 2112
| 7.5 | 1792 | 1843 | 1894 | 1945 | 1996 | 2047 | 2098 | 2149 | 2200 | 2251 | 2302 | 2353 | 2404 | 2454 | 2505 | 2556 | 2608
| 8 | 2183 | 2245 | 2306 | 2368 | 2430 | 2491 | 2553 | 2615 | 2676 | 2738 | 2799 | 2860 | 2922 | 2983 | 3042 | 3100 | 3156
| 8.5 | 2601 | 2674 | 2747 | 2820 | 2893 | 2966 | 3039 | 3112 | 3185 | 3258 | 3330 | 3403 | 3476 | 3546 | 3607 | 3665 | 3722
| 9 | 3023 | 3108 | 3192 | 3277 | 3361 | 3446 | 3530 | 3614 | 3698 | 3782 | 3866 | 3950 | 4034 | 4110 | 4168 | 4223 | 4276
| 9.5 | 3435 | 3531 | 3626 | 3722 | 3817 | 3912 | 4007 | 4103 | 4199 | 4295 | 4387 | 4478 | 4570 | 4645 | 4693 | 4736 | 4777
| 10 | 3826 | 3933 | 4038 | 4144 | 4251 | 4357 | 4464 | 4564 | 4664 | 4764 | 4843 | 4919 | 4995 | 5056 | 5091 | 5120 | 5148
| 10.5 | 4194 | 4309 | 4426 | 4543 | 4655 | 4762 | 4868 | 4952 | 5035 | 5117 | 5180 | 5241 | 5302 | 5348 | 5371 | 5390 | 5407
| 11 | 4542 | 4668 | 4783 | 4896 | 4995 | 5083 | 5170 | 5238 | 5304 | 5370 | 5417 | 5462 | 5507 | 5539 | 5553 | 5563 | 5573
| 11.5 | 4863 | 4981 | 5078 | 5171 | 5251 | 5321 | 5392 | 5443 | 5492 | 5541 | 5573 | 5603 | 5633 | 5652 | 5659 | 5663 | 5666
| 12 | 5125 | 5223 | 5301 | 5376 | 5439 | 5492 | 5546 | 5580 | 5614 | 5647 | 5663 | 5677 | 5691 | 5699 | 5700 | 5700 | 5700
| 12.5 | 5327 | 5406 | 5467 | 5525 | 5570 | 5607 | 5644 | 5662 | 5679 | 5696 | 5699 | 5699 | 5700 | 5700 | 5700 | 5700 | 5700
| 13 | 5479 | 5540 | 5584 | 5624 | 5653 | 5673 | 5693 | 5697 | 5699 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700
| 13.5 | 5587 | 5631 | 5658 | 5681 | 5694 | 5697 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700
| 14 | 5657 | 5684 | 5693 | 5699 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700
| 14.5 | 5692 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700
| 15 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700
| 15.5 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700
| 16 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700
| 16.5 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700
| 17 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700
| 17.5 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700
| 18 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700
| 18.5 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700
| 19 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700
| 19.5 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700
| 20 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700 | 5700
| 20.5 | 5586 | 5586 | 5586 | 5586 | 5586 | 5586 | 5586 | 5586 | 5586 | 5586 | 5586 | 5586 | 5586 | 5586 | 5586 | 5586 | 5586
| 21 | 5455 | 5455 | 5455 | 5455 | 5455 | 5455 | 5455 | 5455 | 5455 | 5455 | 5455 | 5455 | 5455 | 5455 | 5455 | 5455 | 5455
| 21.5 | 5307 | 5307 | 5307 | 5307 | 5307 | 5307 | 5307 | 5307 | 5307 | 5307 | 5307 | 5307 | 5307 | 5307 | 5307 | 5307 | 5307
| 22 | 5153 | 5153 | 5153 | 5153 | 5153 | 5153 | 5153 | 5153 | 5153 | 5153 | 5153 | 5153 | 5153 | 5153 | 5153 | 5153 | 5153
| 22.5 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005
| 23 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856
| 23.5 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708
| 24 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560
| 24.5 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418
| 25 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269
| 25.5 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121
| 26 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764
| 3.5 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208
| 4 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819
| 4.5 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639
| 5 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875
| 5.5 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458
| 6 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181
| 6.5 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042
| 7 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972 | 0.55972
| 7.5 | 0.55347 | 0.55347 | 0.55347 | 0.55347 | 0.55347 | 0.55347 | 0.55347 | 0.55347 | 0.55347 | 0.55347 | 0.55347 | 0.55347 | 0.55347 | 0.55347 | 0.55139 | 0.54931 | 0.54792
| 8 | 0.53819 | 0.53819 | 0.53819 | 0.53819 | 0.53819 | 0.53819 | 0.53819 | 0.53819 | 0.53819 | 0.53819 | 0.53819 | 0.53819 | 0.53819 | 0.5375 | 0.53403 | 0.53125 | 0.52847
| 8.5 | 0.51736 | 0.51736 | 0.51736 | 0.51736 | 0.51736 | 0.51736 | 0.51736 | 0.51736 | 0.51736 | 0.51736 | 0.51736 | 0.51736 | 0.51667 | 0.51597 | 0.51111 | 0.50694 | 0.50347
| 9 | 0.49236 | 0.49236 | 0.49236 | 0.49236 | 0.49236 | 0.49236 | 0.49236 | 0.49236 | 0.49236 | 0.49236 | 0.49097 | 0.48958 | 0.48819 | 0.48611 | 0.48125 | 0.47569 | 0.47153
| 9.5 | 0.46597 | 0.46597 | 0.46597 | 0.46597 | 0.46528 | 0.46528 | 0.46458 | 0.46389 | 0.4625 | 0.46111 | 0.45903 | 0.45694 | 0.45486 | 0.45208 | 0.44653 | 0.44097 | 0.43611
| 10 | 0.43819 | 0.43819 | 0.4375 | 0.43681 | 0.43611 | 0.43472 | 0.43333 | 0.43125 | 0.42917 | 0.42708 | 0.425 | 0.42222 | 0.41944 | 0.41597 | 0.41042 | 0.40486 | 0.39931
| 10.5 | 0.40903 | 0.40833 | 0.40694 | 0.40556 | 0.40347 | 0.40208 | 0.4 | 0.39722 | 0.39444 | 0.39236 | 0.38958 | 0.38611 | 0.38333 | 0.37986 | 0.37361 | 0.36806 | 0.3625
| 11 | 0.37847 | 0.37708 | 0.375 | 0.37292 | 0.37083 | 0.36806 | 0.36597 | 0.36319 | 0.36042 | 0.35764 | 0.35417 | 0.35069 | 0.34792 | 0.34375 | 0.3375 | 0.33194 | 0.32639
| 11.5 | 0.34722 | 0.34514 | 0.34306 | 0.34028 | 0.3375 | 0.33472 | 0.33264 | 0.32917 | 0.32569 | 0.32292 | 0.31944 | 0.31597 | 0.3125 | 0.30903 | 0.30278 | 0.29653 | 0.29097
| 12 | 0.31667 | 0.31458 | 0.31181 | 0.30903 | 0.30556 | 0.30278 | 0.3 | 0.29653 | 0.29306 | 0.29028 | 0.28611 | 0.28264 | 0.27917 | 0.27569 | 0.26944 | 0.26389 | 0.25833
| 12.5 | 0.28819 | 0.28542 | 0.28264 | 0.27917 | 0.27639 | 0.27292 | 0.27014 | 0.26667 | 0.26319 | 0.25972 | 0.25625 | 0.25208 | 0.24861 | 0.24514 | 0.23958 | 0.23472 | 0.22986
| 13 | 0.26181 | 0.25903 | 0.25625 | 0.25278 | 0.25 | 0.24653 | 0.24306 | 0.23958 | 0.23611 | 0.23264 | 0.22917 | 0.225 | 0.22153 | 0.21736 | 0.21319 | 0.20833 | 0.20417
| 13.5 | 0.23889 | 0.23542 | 0.23264 | 0.22917 | 0.22569 | 0.22222 | 0.21944 | 0.21528 | 0.21181 | 0.20833 | 0.20486 | 0.20069 | 0.19722 | 0.19375 | 0.18958 | 0.18542 | 0.18125
| 14 | 0.21736 | 0.21458 | 0.21111 | 0.20764 | 0.20417 | 0.20069 | 0.19722 | 0.19375 | 0.19028 | 0.18681 | 0.18264 | 0.17917 | 0.17569 | 0.17222 | 0.16806 | 0.16458 | 0.16111
| 14.5 | 0.19861 | 0.19514 | 0.19167 | 0.18819 | 0.18472 | 0.18125 | 0.17778 | 0.17431 | 0.17083 | 0.16736 | 0.16319 | 0.15972 | 0.15625 | 0.15278 | 0.15 | 0.14653 | 0.14375
| 15 | 0.18125 | 0.17778 | 0.17431 | 0.17083 | 0.16736 | 0.16389 | 0.16042 | 0.15694 | 0.15278 | 0.14931 | 0.14653 | 0.14306 | 0.13958 | 0.13681 | 0.13403 | 0.13125 | 0.12917
| 15.5 | 0.16528 | 0.16181 | 0.15833 | 0.15486 | 0.15139 | 0.14792 | 0.14444 | 0.14097 | 0.1375 | 0.13472 | 0.13125 | 0.12847 | 0.12639 | 0.12361 | 0.12083 | 0.11875 | 0.11667
| 16 | 0.15069 | 0.14792 | 0.14375 | 0.14097 | 0.1375 | 0.13403 | 0.13056 | 0.12708 | 0.12431 | 0.12153 | 0.11875 | 0.11667 | 0.11389 | 0.11181 | 0.10972 | 0.10764 | 0.10556
| 16.5 | 0.13819 | 0.13472 | 0.13125 | 0.12778 | 0.12431 | 0.12153 | 0.11875 | 0.11597 | 0.11319 | 0.11111 | 0.10833 | 0.10625 | 0.10417 | 0.10208 | 0.1 | 0.098611 | 0.096528
| 17 | 0.12708 | 0.12361 | 0.12014 | 0.11736 | 0.11389 | 0.11111 | 0.10903 | 0.10625 | 0.10417 | 0.10139 | 0.099306 | 0.097917 | 0.095833 | 0.09375 | 0.092361 | 0.090278 | 0.088889
| 17.5 | 0.11667 | 0.11389 | 0.11042 | 0.10764 | 0.10556 | 0.10278 | 0.10069 | 0.097917 | 0.095833 | 0.09375 | 0.092361 | 0.090278 | 0.088194 | 0.086806 | 0.085417 | 0.083333 | 0.081944
| 18 | 0.10833 | 0.10556 | 0.10278 | 0.1 | 0.097917 | 0.095833 | 0.093056 | 0.090972 | 0.089583 | 0.0875 | 0.085417 | 0.084028 | 0.082639 | 0.080556 | 0.079167 | 0.077778 | 0.076389
| 18.5 | 0.10139 | 0.098611 | 0.095833 | 0.09375 | 0.091667 | 0.089583 | 0.0875 | 0.085417 | 0.083333 | 0.081944 | 0.080556 | 0.078472 | 0.077083 | 0.075694 | 0.074306 | 0.072917 | 0.071528
| 19 | 0.095139 | 0.093056 | 0.090278 | 0.088194 | 0.086111 | 0.084028 | 0.082639 | 0.080556 | 0.079167 | 0.077083 | 0.075694 | 0.074306 | 0.072917 | 0.071528 | 0.070139 | 0.099 | 0.098
| 19.5 | 0.090278 | 0.088194 | 0.085417 | 0.083333 | 0.081944 | 0.079861 | 0.077778 | 0.076389 | 0.075 | 0.072917 | 0.071528 | 0.070139 | 0.099 | 0.098 | 0.096 | 0.094 | 0.093
| 20 | 0.086111 | 0.083333 | 0.08125 | 0.079861 | 0.077778 | 0.075694 | 0.074306 | 0.072917 | 0.071528 | 0.070139 | 0.099 | 0.097 | 0.095 | 0.093 | 0.091 | 0.09 | 0.088
| 20.5 | 0.079167 | 0.076389 | 0.075 | 0.073611 | 0.071528 | 0.069444 | 0.098 | 0.097 | 0.095 | 0.093 | 0.091 | 0.089 | 0.087 | 0.086 | 0.084 | 0.083 | 0.081
| 21 | 0.072222 | 0.070139 | 0.098 | 0.097 | 0.094 | 0.092 | 0.09 | 0.088 | 0.087 | 0.085 | 0.083 | 0.082 | 0.08 | 0.078 | 0.077 | 0.076 | 0.074
| 21.5 | 0.094 | 0.091 | 0.089 | 0.088 | 0.085 | 0.083 | 0.082 | 0.08 | 0.078 | 0.077 | 0.075 | 0.074 | 0.072 | 0.071 | 0.069 | 0.069 | 0.067
| 22 | 0.086 | 0.084 | 0.082 | 0.08 | 0.078 | 0.076 | 0.075 | 0.073 | 0.072 | 0.07 | 0.069 | 0.068 | 0.066 | 0.065 | 0.063 | 0.063 | 0.061
| 22.5 | 0.079 | 0.077 | 0.075 | 0.073 | 0.071 | 0.07 | 0.068 | 0.067 | 0.066 | 0.064 | 0.063 | 0.062 | 0.061 | 0.059 | 0.058 | 0.057 | 0.056
| 23 | 0.073 | 0.07 | 0.069 | 0.067 | 0.066 | 0.064 | 0.063 | 0.062 | 0.06 | 0.059 | 0.058 | 0.057 | 0.056 | 0.054 | 0.053 | 0.053 | 0.052
| 23.5 | 0.066 | 0.064 | 0.062 | 0.061 | 0.059 | 0.058 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053 | 0.052 | 0.05 | 0.049 | 0.048 | 0.048 | 0.047
| 24 | 0.061 | 0.059 | 0.057 | 0.056 | 0.055 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043
| 24.5 | 0.056 | 0.054 | 0.053 | 0.052 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.041 | 0.04
| 25 | 0.052 | 0.05 | 0.049 | 0.048 | 0.047 | 0.045 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.04 | 0.039 | 0.038 | 0.038 | 0.037
| 25.5 | 0.048 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.04 | 0.039 | 0.038 | 0.037 | 0.037 | 0.036 | 0.035 | 0.035 | 0.034
| 26 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.038 | 0.038 | 0.037 | 0.036 | 0.035 | 0.035 | 0.034 | 0.033 | 0.033 | 0.032 | 0.032