## Sheet1
PROPERTIES
General
Name | Nordex N163/5.X Class B 108m 4,29MW
Manufacturer | Nordex
Hub Height | 108
Power
Rated Power | 4290
Peak Power | 4290
Power Regulation Type | Pitch
Voltage | 750
Rotor
Rotor diameter | 163
Number of blades | 3
Rated RPM | 11.8
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 26
Restart Wind Speed | 25.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 45
High Temperature Restart | 40
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | B
Values
Certification | IEC 3rd Edition
Vave | 6.5-8
Vref | 38.8-40.3
Design TI | 0.16

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 31 | 33 | 35 | 37 | 40 | 42 | 44 | 46 | 49
| 3.5 | 126 | 130 | 134 | 139 | 143 | 148 | 152 | 156 | 161
| 4 | 253 | 260 | 267 | 275 | 282 | 289 | 296 | 304 | 311
| 4.5 | 410 | 421 | 432 | 442 | 453 | 464 | 475 | 486 | 497
| 5 | 598 | 613 | 628 | 643 | 658 | 673 | 688 | 703 | 719
| 5.5 | 821 | 841 | 861 | 881 | 902 | 922 | 942 | 962 | 982
| 6 | 1085 | 1111 | 1137 | 1163 | 1190 | 1216 | 1242 | 1268 | 1294
| 6.5 | 1378 | 1410 | 1443 | 1476 | 1509 | 1541 | 1574 | 1607 | 1639
| 7 | 1672 | 1711 | 1750 | 1790 | 1829 | 1868 | 1908 | 1947 | 1986
| 7.5 | 1951 | 1997 | 2042 | 2088 | 2134 | 2179 | 2225 | 2270 | 2316
| 8 | 2210 | 2261 | 2313 | 2364 | 2416 | 2467 | 2518 | 2570 | 2621
| 8.5 | 2451 | 2508 | 2565 | 2622 | 2678 | 2735 | 2792 | 2849 | 2905
| 9 | 2678 | 2740 | 2802 | 2864 | 2925 | 2987 | 3049 | 3111 | 3173
| 9.5 | 2895 | 2962 | 3029 | 3095 | 3162 | 3229 | 3295 | 3362 | 3429
| 10 | 3108 | 3180 | 3251 | 3323 | 3394 | 3466 | 3538 | 3608 | 3675
| 10.5 | 3319 | 3395 | 3471 | 3548 | 3624 | 3695 | 3766 | 3828 | 3883
| 11 | 3520 | 3602 | 3683 | 3757 | 3830 | 3887 | 3944 | 3994 | 4038
| 11.5 | 3715 | 3793 | 3868 | 3929 | 3988 | 4034 | 4080 | 4118 | 4150
| 12 | 3885 | 3951 | 4013 | 4062 | 4110 | 4144 | 4178 | 4206 | 4227
| 12.5 | 4020 | 4074 | 4124 | 4161 | 4197 | 4221 | 4244 | 4261 | 4272
| 13 | 4123 | 4165 | 4203 | 4230 | 4255 | 4268 | 4281 | 4287 | 4289
| 13.5 | 4197 | 4227 | 4255 | 4270 | 4285 | 4287 | 4290 | 4290 | 4290
| 14 | 4246 | 4266 | 4282 | 4287 | 4290 | 4290 | 4290 | 4290 | 4290
| 14.5 | 4277 | 4285 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290
| 15 | 4289 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290
| 15.5 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290
| 16 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290
| 16.5 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290
| 17 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290
| 17.5 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290
| 18 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290
| 18.5 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290
| 19 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290
| 19.5 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290
| 20 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290
| 20.5 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290
| 21 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290
| 21.5 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290
| 22 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290
| 22.5 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290
| 23 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290
| 23.5 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290
| 24 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290
| 24.5 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290
| 25 | 4246 | 4246 | 4246 | 4246 | 4246 | 4246 | 4246 | 4246 | 4246
| 25.5 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121
| 26 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764
| 3.5 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208
| 4 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819
| 4.5 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639
| 5 | 0.56944 | 0.56944 | 0.56944 | 0.56944 | 0.56944 | 0.56944 | 0.56944 | 0.56944 | 0.56944
| 5.5 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181
| 6 | 0.54167 | 0.54167 | 0.54167 | 0.54167 | 0.54167 | 0.54167 | 0.54167 | 0.54167 | 0.54167
| 6.5 | 0.5125 | 0.5125 | 0.5125 | 0.5125 | 0.5125 | 0.5125 | 0.5125 | 0.5125 | 0.5125
| 7 | 0.47847 | 0.47847 | 0.47847 | 0.47847 | 0.47847 | 0.47847 | 0.47847 | 0.47847 | 0.47847
| 7.5 | 0.44167 | 0.44167 | 0.44167 | 0.44167 | 0.44167 | 0.44167 | 0.44167 | 0.44167 | 0.44167
| 8 | 0.40417 | 0.40417 | 0.40417 | 0.40417 | 0.40417 | 0.40417 | 0.40417 | 0.40417 | 0.40417
| 8.5 | 0.36597 | 0.36597 | 0.36597 | 0.36597 | 0.36597 | 0.36597 | 0.36597 | 0.36597 | 0.36597
| 9 | 0.32917 | 0.32917 | 0.32917 | 0.32917 | 0.32917 | 0.32917 | 0.32917 | 0.32917 | 0.32917
| 9.5 | 0.29653 | 0.29653 | 0.29653 | 0.29653 | 0.29653 | 0.29653 | 0.29653 | 0.29583 | 0.29514
| 10 | 0.26806 | 0.26806 | 0.26806 | 0.26806 | 0.26736 | 0.26736 | 0.26667 | 0.26597 | 0.26458
| 10.5 | 0.24306 | 0.24306 | 0.24306 | 0.24236 | 0.24167 | 0.24097 | 0.23958 | 0.23889 | 0.2375
| 11 | 0.22153 | 0.22083 | 0.22014 | 0.21944 | 0.21806 | 0.21736 | 0.21597 | 0.21528 | 0.21389
| 11.5 | 0.20139 | 0.20069 | 0.2 | 0.19861 | 0.19792 | 0.19653 | 0.19514 | 0.19375 | 0.19236
| 12 | 0.18333 | 0.18264 | 0.18125 | 0.18056 | 0.17917 | 0.17778 | 0.17639 | 0.175 | 0.17292
| 12.5 | 0.16736 | 0.16597 | 0.16528 | 0.16389 | 0.1625 | 0.16111 | 0.15972 | 0.15764 | 0.15625
| 13 | 0.15278 | 0.15139 | 0.15 | 0.14861 | 0.14722 | 0.14583 | 0.14444 | 0.14236 | 0.14097
| 13.5 | 0.13958 | 0.13819 | 0.13681 | 0.13542 | 0.13403 | 0.13264 | 0.13056 | 0.12917 | 0.12708
| 14 | 0.12778 | 0.12639 | 0.125 | 0.12361 | 0.12222 | 0.12014 | 0.11875 | 0.11667 | 0.11528
| 14.5 | 0.11736 | 0.11597 | 0.11389 | 0.1125 | 0.11111 | 0.10903 | 0.10764 | 0.10625 | 0.10417
| 15 | 0.10764 | 0.10556 | 0.10417 | 0.10278 | 0.10139 | 0.099306 | 0.097917 | 0.095833 | 0.094444
| 15.5 | 0.098611 | 0.097222 | 0.095139 | 0.09375 | 0.092361 | 0.090278 | 0.088889 | 0.0875 | 0.085417
| 16 | 0.090278 | 0.088889 | 0.0875 | 0.085417 | 0.084028 | 0.082639 | 0.080556 | 0.079167 | 0.077778
| 16.5 | 0.083333 | 0.08125 | 0.079861 | 0.078472 | 0.077083 | 0.075694 | 0.073611 | 0.072222 | 0.070833
| 17 | 0.077083 | 0.075 | 0.073611 | 0.072222 | 0.070833 | 0.069444 | 0.098 | 0.096 | 0.094
| 17.5 | 0.071528 | 0.069444 | 0.098 | 0.096 | 0.094 | 0.093 | 0.091 | 0.089 | 0.088
| 18 | 0.096 | 0.094 | 0.092 | 0.09 | 0.088 | 0.086 | 0.085 | 0.083 | 0.082
| 18.5 | 0.09 | 0.088 | 0.086 | 0.084 | 0.083 | 0.081 | 0.08 | 0.078 | 0.077
| 19 | 0.085 | 0.083 | 0.081 | 0.08 | 0.078 | 0.077 | 0.075 | 0.074 | 0.073
| 19.5 | 0.08 | 0.079 | 0.077 | 0.076 | 0.074 | 0.073 | 0.071 | 0.07 | 0.069
| 20 | 0.077 | 0.075 | 0.074 | 0.072 | 0.071 | 0.069 | 0.068 | 0.067 | 0.066
| 20.5 | 0.071 | 0.069 | 0.068 | 0.066 | 0.065 | 0.063 | 0.063 | 0.062 | 0.061
| 21 | 0.065 | 0.063 | 0.062 | 0.061 | 0.06 | 0.058 | 0.057 | 0.056 | 0.056
| 21.5 | 0.059 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053 | 0.052 | 0.051 | 0.05
| 22 | 0.054 | 0.052 | 0.052 | 0.05 | 0.049 | 0.048 | 0.047 | 0.047 | 0.046
| 22.5 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.043 | 0.042
| 23 | 0.045 | 0.044 | 0.043 | 0.042 | 0.042 | 0.04 | 0.04 | 0.039 | 0.039
| 23.5 | 0.041 | 0.04 | 0.039 | 0.038 | 0.038 | 0.037 | 0.036 | 0.036 | 0.035
| 24 | 0.038 | 0.037 | 0.036 | 0.035 | 0.035 | 0.034 | 0.033 | 0.033 | 0.032
| 24.5 | 0.035 | 0.034 | 0.033 | 0.032 | 0.032 | 0.031 | 0.031 | 0.03 | 0.03
| 25 | 0.032 | 0.031 | 0.031 | 0.03 | 0.03 | 0.029 | 0.028 | 0.028 | 0.028
| 25.5 | 0.03 | 0.029 | 0.028 | 0.028 | 0.027 | 0.027 | 0.026 | 0.026 | 0.025
| 26 | 0.028 | 0.027 | 0.026 | 0.026 | 0.025 | 0.025 | 0.024 | 0.024 | 0.024