## Sheet1
PROPERTIES
General
Name | Nordex N163/5.X Class B 4,29MW
Manufacturer | Nordex
Hub Height | 118 | 120 | 148 | 159 | 164
Power
Rated Power | 4290
Peak Power | 4290
Power Regulation Type | Pitch
Voltage | 750
Rotor
Rotor diameter | 163
Number of blades | 3
Rated RPM | 11.8
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 26
Restart Wind Speed | 25.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 45
High Temperature Restart | 40
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | B
Values
Certification | IEC 3rd Edition
Vave | 6.5-8
Vref | 38.8-40.3
Design TI | 0.16

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 37 | 39 | 41 | 44 | 46 | 48 | 50 | 53 | 55
| 3.5 | 133 | 137 | 142 | 146 | 151 | 155 | 159 | 164 | 168
| 4 | 261 | 268 | 276 | 283 | 290 | 298 | 305 | 312 | 320
| 4.5 | 420 | 431 | 441 | 452 | 463 | 474 | 485 | 496 | 507
| 5 | 609 | 624 | 639 | 655 | 670 | 685 | 700 | 716 | 731
| 5.5 | 834 | 854 | 875 | 895 | 915 | 936 | 956 | 976 | 997
| 6 | 1100 | 1126 | 1153 | 1179 | 1205 | 1232 | 1258 | 1284 | 1310
| 6.5 | 1395 | 1428 | 1460 | 1493 | 1526 | 1559 | 1592 | 1625 | 1658
| 7 | 1690 | 1730 | 1769 | 1809 | 1848 | 1888 | 1927 | 1967 | 2006
| 7.5 | 1971 | 2017 | 2063 | 2108 | 2154 | 2200 | 2246 | 2292 | 2337
| 8 | 2231 | 2283 | 2334 | 2386 | 2437 | 2489 | 2540 | 2592 | 2643
| 8.5 | 2473 | 2530 | 2587 | 2644 | 2701 | 2758 | 2815 | 2871 | 2928
| 9 | 2700 | 2762 | 2824 | 2886 | 2948 | 3010 | 3072 | 3134 | 3196
| 9.5 | 2918 | 2985 | 3052 | 3119 | 3185 | 3252 | 3319 | 3385 | 3453
| 10 | 3131 | 3203 | 3275 | 3346 | 3417 | 3490 | 3562 | 3630 | 3698
| 10.5 | 3342 | 3418 | 3494 | 3571 | 3646 | 3717 | 3788 | 3845 | 3900
| 11 | 3544 | 3625 | 3705 | 3778 | 3847 | 3904 | 3962 | 4008 | 4051
| 11.5 | 3738 | 3814 | 3886 | 3946 | 4002 | 4047 | 4093 | 4128 | 4160
| 12 | 3906 | 3968 | 4027 | 4075 | 4120 | 4154 | 4188 | 4212 | 4234
| 12.5 | 4037 | 4087 | 4135 | 4171 | 4204 | 4227 | 4251 | 4264 | 4275
| 13 | 4136 | 4175 | 4211 | 4236 | 4258 | 4271 | 4284 | 4288 | 4289
| 13.5 | 4207 | 4234 | 4259 | 4274 | 4286 | 4288 | 4290 | 4290 | 4290
| 14 | 4253 | 4270 | 4284 | 4288 | 4290 | 4290 | 4290 | 4290 | 4290
| 14.5 | 4281 | 4286 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290
| 15 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290
| 15.5 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290
| 16 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290
| 16.5 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290
| 17 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290
| 17.5 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290
| 18 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290
| 18.5 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290
| 19 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290
| 19.5 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290
| 20 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290
| 20.5 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290
| 21 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290
| 21.5 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290
| 22 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290
| 22.5 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290
| 23 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290
| 23.5 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290
| 24 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290
| 24.5 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290 | 4290
| 25 | 4246 | 4246 | 4246 | 4246 | 4246 | 4246 | 4246 | 4246 | 4246
| 25.5 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121
| 26 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764
| 3.5 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208
| 4 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819
| 4.5 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639
| 5 | 0.56944 | 0.56944 | 0.56944 | 0.56944 | 0.56944 | 0.56944 | 0.56944 | 0.56944 | 0.56944
| 5.5 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181
| 6 | 0.54167 | 0.54167 | 0.54167 | 0.54167 | 0.54167 | 0.54167 | 0.54167 | 0.54167 | 0.54167
| 6.5 | 0.5125 | 0.5125 | 0.5125 | 0.5125 | 0.5125 | 0.5125 | 0.5125 | 0.5125 | 0.5125
| 7 | 0.47847 | 0.47847 | 0.47847 | 0.47847 | 0.47847 | 0.47847 | 0.47847 | 0.47847 | 0.47847
| 7.5 | 0.44167 | 0.44167 | 0.44167 | 0.44167 | 0.44167 | 0.44167 | 0.44167 | 0.44167 | 0.44167
| 8 | 0.40417 | 0.40417 | 0.40417 | 0.40417 | 0.40417 | 0.40417 | 0.40417 | 0.40417 | 0.40417
| 8.5 | 0.36597 | 0.36597 | 0.36597 | 0.36597 | 0.36597 | 0.36597 | 0.36597 | 0.36597 | 0.36597
| 9 | 0.32917 | 0.32917 | 0.32917 | 0.32917 | 0.32917 | 0.32917 | 0.32917 | 0.32917 | 0.32917
| 9.5 | 0.29653 | 0.29653 | 0.29653 | 0.29653 | 0.29653 | 0.29653 | 0.29583 | 0.29583 | 0.29514
| 10 | 0.26806 | 0.26806 | 0.26806 | 0.26806 | 0.26736 | 0.26667 | 0.26597 | 0.26528 | 0.26458
| 10.5 | 0.24306 | 0.24306 | 0.24236 | 0.24236 | 0.24167 | 0.24028 | 0.23958 | 0.23819 | 0.2375
| 11 | 0.22083 | 0.22083 | 0.22014 | 0.21875 | 0.21806 | 0.21667 | 0.21597 | 0.21458 | 0.21319
| 11.5 | 0.20139 | 0.20069 | 0.19931 | 0.19861 | 0.19722 | 0.19583 | 0.19444 | 0.19306 | 0.19167
| 12 | 0.18333 | 0.18194 | 0.18125 | 0.17986 | 0.17847 | 0.17708 | 0.17569 | 0.17431 | 0.17292
| 12.5 | 0.16736 | 0.16597 | 0.16458 | 0.16319 | 0.16181 | 0.16042 | 0.15903 | 0.15764 | 0.15556
| 13 | 0.15278 | 0.15139 | 0.15 | 0.14861 | 0.14722 | 0.14514 | 0.14375 | 0.14236 | 0.14028
| 13.5 | 0.13958 | 0.13819 | 0.13681 | 0.13542 | 0.13333 | 0.13194 | 0.13056 | 0.12847 | 0.12708
| 14 | 0.12778 | 0.12639 | 0.12431 | 0.12292 | 0.12153 | 0.12014 | 0.11806 | 0.11667 | 0.11458
| 14.5 | 0.11667 | 0.11528 | 0.11389 | 0.1125 | 0.11042 | 0.10903 | 0.10764 | 0.10556 | 0.10347
| 15 | 0.10694 | 0.10556 | 0.10417 | 0.10208 | 0.10069 | 0.099306 | 0.097222 | 0.095833 | 0.09375
| 15.5 | 0.097917 | 0.096528 | 0.095139 | 0.09375 | 0.091667 | 0.090278 | 0.088194 | 0.086806 | 0.085417
| 16 | 0.090278 | 0.088194 | 0.086806 | 0.085417 | 0.083333 | 0.081944 | 0.080556 | 0.079167 | 0.077083
| 16.5 | 0.082639 | 0.08125 | 0.079861 | 0.077778 | 0.076389 | 0.075 | 0.073611 | 0.072222 | 0.070833
| 17 | 0.076389 | 0.075 | 0.073611 | 0.071528 | 0.070139 | 0.099 | 0.098 | 0.096 | 0.094
| 17.5 | 0.070833 | 0.069444 | 0.098 | 0.096 | 0.094 | 0.092 | 0.09 | 0.089 | 0.087
| 18 | 0.095 | 0.093 | 0.091 | 0.089 | 0.088 | 0.086 | 0.084 | 0.083 | 0.081
| 18.5 | 0.089 | 0.087 | 0.086 | 0.084 | 0.082 | 0.081 | 0.079 | 0.078 | 0.076
| 19 | 0.084 | 0.082 | 0.081 | 0.079 | 0.078 | 0.076 | 0.075 | 0.073 | 0.072
| 19.5 | 0.08 | 0.078 | 0.077 | 0.075 | 0.074 | 0.072 | 0.071 | 0.07 | 0.069
| 20 | 0.076 | 0.075 | 0.073 | 0.072 | 0.07 | 0.069 | 0.068 | 0.067 | 0.066
| 20.5 | 0.07 | 0.069 | 0.067 | 0.066 | 0.064 | 0.063 | 0.063 | 0.062 | 0.061
| 21 | 0.064 | 0.063 | 0.061 | 0.061 | 0.059 | 0.058 | 0.057 | 0.056 | 0.056
| 21.5 | 0.058 | 0.057 | 0.056 | 0.055 | 0.053 | 0.053 | 0.052 | 0.051 | 0.05
| 22 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.047 | 0.046
| 22.5 | 0.048 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.043 | 0.042
| 23 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.04 | 0.039 | 0.039
| 23.5 | 0.04 | 0.04 | 0.039 | 0.038 | 0.037 | 0.037 | 0.036 | 0.036 | 0.035
| 24 | 0.037 | 0.037 | 0.036 | 0.035 | 0.034 | 0.034 | 0.033 | 0.033 | 0.032
| 24.5 | 0.034 | 0.034 | 0.033 | 0.032 | 0.032 | 0.031 | 0.031 | 0.03 | 0.03
| 25 | 0.032 | 0.031 | 0.03 | 0.03 | 0.029 | 0.029 | 0.028 | 0.028 | 0.028
| 25.5 | 0.029 | 0.029 | 0.028 | 0.028 | 0.027 | 0.027 | 0.026 | 0.026 | 0.025
| 26 | 0.027 | 0.027 | 0.026 | 0.026 | 0.025 | 0.025 | 0.024 | 0.024 | 0.024