## Sheet1
PROPERTIES
General
Name | Nordex N163/5.X Class B 3,99MW
Manufacturer | Nordex
Hub Height | 118 | 120 | 148 | 159 | 164
Power
Rated Power | 3990
Peak Power | 3990
Power Regulation Type | Pitch
Voltage | 750
Rotor
Rotor diameter | 163
Number of blades | 3
Rated RPM | 11.8
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 26
Restart Wind Speed | 25.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 45
High Temperature Restart | 40
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | B
Values
Certification | IEC 3rd Edition
Vave | 6.5-8
Vref | 38.8-40.3
Design TI | 0.16

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 37 | 39 | 41 | 44 | 46 | 48 | 50 | 53 | 55
| 3.5 | 133 | 137 | 142 | 146 | 150 | 155 | 159 | 164 | 168
| 4 | 261 | 268 | 276 | 283 | 290 | 298 | 305 | 312 | 320
| 4.5 | 420 | 431 | 441 | 452 | 463 | 474 | 485 | 496 | 507
| 5 | 609 | 624 | 639 | 655 | 670 | 685 | 700 | 716 | 731
| 5.5 | 834 | 854 | 875 | 895 | 915 | 936 | 956 | 976 | 997
| 6 | 1095 | 1121 | 1147 | 1173 | 1199 | 1225 | 1252 | 1278 | 1304
| 6.5 | 1365 | 1397 | 1429 | 1462 | 1494 | 1526 | 1558 | 1591 | 1623
| 7 | 1626 | 1664 | 1702 | 1740 | 1779 | 1817 | 1855 | 1893 | 1931
| 7.5 | 1867 | 1911 | 1954 | 1998 | 2041 | 2085 | 2128 | 2172 | 2215
| 8 | 2091 | 2140 | 2188 | 2237 | 2285 | 2333 | 2382 | 2430 | 2479
| 8.5 | 2300 | 2353 | 2407 | 2460 | 2513 | 2566 | 2619 | 2672 | 2725
| 9 | 2499 | 2557 | 2614 | 2672 | 2729 | 2787 | 2844 | 2902 | 2959
| 9.5 | 2694 | 2756 | 2818 | 2879 | 2941 | 3003 | 3065 | 3126 | 3188
| 10 | 2886 | 2952 | 3018 | 3084 | 3150 | 3216 | 3283 | 3349 | 3412
| 10.5 | 3069 | 3140 | 3210 | 3280 | 3351 | 3421 | 3486 | 3551 | 3602
| 11 | 3245 | 3319 | 3394 | 3468 | 3535 | 3601 | 3654 | 3707 | 3747
| 11.5 | 3418 | 3495 | 3564 | 3632 | 3686 | 3740 | 3782 | 3824 | 3854
| 12 | 3577 | 3646 | 3703 | 3758 | 3802 | 3845 | 3876 | 3908 | 3928
| 12.5 | 3705 | 3762 | 3808 | 3852 | 3886 | 3918 | 3940 | 3961 | 3972
| 13 | 3803 | 3849 | 3884 | 3918 | 3941 | 3963 | 3975 | 3987 | 3989
| 13.5 | 3876 | 3912 | 3937 | 3960 | 3974 | 3986 | 3988 | 3990 | 3990
| 14 | 3930 | 3955 | 3970 | 3984 | 3988 | 3990 | 3990 | 3990 | 3990
| 14.5 | 3966 | 3982 | 3987 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990
| 15 | 3985 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990
| 15.5 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990
| 16 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990
| 16.5 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990
| 17 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990
| 17.5 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990
| 18 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990
| 18.5 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990
| 19 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990
| 19.5 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990
| 20 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990
| 20.5 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990
| 21 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990
| 21.5 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990
| 22 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990
| 22.5 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990
| 23 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990
| 23.5 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990
| 24 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990
| 24.5 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990
| 25 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990
| 25.5 | 3987 | 3987 | 3987 | 3987 | 3987 | 3987 | 3987 | 3987 | 3987
| 26 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764
| 3.5 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208
| 4 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819
| 4.5 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639
| 5 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875
| 5.5 | 0.55347 | 0.55347 | 0.55347 | 0.55347 | 0.55347 | 0.55347 | 0.55347 | 0.55347 | 0.55347
| 6 | 0.52569 | 0.52569 | 0.52569 | 0.52569 | 0.52569 | 0.52569 | 0.52569 | 0.52569 | 0.52569
| 6.5 | 0.49097 | 0.49097 | 0.49097 | 0.49097 | 0.49097 | 0.49097 | 0.49097 | 0.49097 | 0.49097
| 7 | 0.45278 | 0.45278 | 0.45278 | 0.45278 | 0.45278 | 0.45278 | 0.45278 | 0.45278 | 0.45278
| 7.5 | 0.41319 | 0.41319 | 0.41319 | 0.41319 | 0.41319 | 0.41319 | 0.41319 | 0.41319 | 0.41319
| 8 | 0.37361 | 0.37361 | 0.37361 | 0.37361 | 0.37361 | 0.37361 | 0.37361 | 0.37361 | 0.37361
| 8.5 | 0.33472 | 0.33472 | 0.33472 | 0.33472 | 0.33472 | 0.33472 | 0.33472 | 0.33472 | 0.33472
| 9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
| 9.5 | 0.26944 | 0.26944 | 0.26944 | 0.26944 | 0.26944 | 0.26944 | 0.26944 | 0.26944 | 0.26875
| 10 | 0.24375 | 0.24375 | 0.24375 | 0.24375 | 0.24306 | 0.24306 | 0.24236 | 0.24236 | 0.24097
| 10.5 | 0.22083 | 0.22083 | 0.22083 | 0.22014 | 0.22014 | 0.21944 | 0.21875 | 0.21806 | 0.21667
| 11 | 0.20139 | 0.20069 | 0.2 | 0.2 | 0.19861 | 0.19792 | 0.19722 | 0.19653 | 0.19514
| 11.5 | 0.18333 | 0.18264 | 0.18194 | 0.18125 | 0.18056 | 0.17917 | 0.17847 | 0.17708 | 0.17569
| 12 | 0.16736 | 0.16667 | 0.16528 | 0.16458 | 0.16319 | 0.1625 | 0.16111 | 0.15972 | 0.15833
| 12.5 | 0.15278 | 0.15139 | 0.15069 | 0.14931 | 0.14861 | 0.14722 | 0.14583 | 0.14444 | 0.14306
| 13 | 0.13958 | 0.13819 | 0.1375 | 0.13611 | 0.13472 | 0.13333 | 0.13194 | 0.13056 | 0.12917
| 13.5 | 0.12778 | 0.12639 | 0.125 | 0.12431 | 0.12292 | 0.12153 | 0.12014 | 0.11875 | 0.11736
| 14 | 0.11667 | 0.11597 | 0.11458 | 0.11319 | 0.11181 | 0.11042 | 0.10903 | 0.10764 | 0.10625
| 14.5 | 0.10694 | 0.10625 | 0.10486 | 0.10347 | 0.10208 | 0.10069 | 0.099306 | 0.097917 | 0.095833
| 15 | 0.098611 | 0.097222 | 0.095833 | 0.094444 | 0.093056 | 0.091667 | 0.090278 | 0.088889 | 0.086806
| 15.5 | 0.090278 | 0.088889 | 0.0875 | 0.086111 | 0.084722 | 0.083333 | 0.081944 | 0.080556 | 0.079167
| 16 | 0.083333 | 0.081944 | 0.080556 | 0.079167 | 0.077778 | 0.076389 | 0.075 | 0.072917 | 0.072222
| 16.5 | 0.076389 | 0.075 | 0.073611 | 0.072222 | 0.070833 | 0.069444 | 0.098 | 0.097 | 0.095
| 17 | 0.070833 | 0.069444 | 0.098 | 0.096 | 0.094 | 0.092 | 0.091 | 0.089 | 0.087
| 17.5 | 0.095 | 0.093 | 0.091 | 0.089 | 0.087 | 0.086 | 0.084 | 0.083 | 0.081
| 18 | 0.089 | 0.087 | 0.085 | 0.083 | 0.082 | 0.08 | 0.079 | 0.077 | 0.076
| 18.5 | 0.083 | 0.081 | 0.08 | 0.078 | 0.077 | 0.075 | 0.074 | 0.072 | 0.071
| 19 | 0.078 | 0.077 | 0.075 | 0.074 | 0.072 | 0.071 | 0.07 | 0.068 | 0.067
| 19.5 | 0.074 | 0.073 | 0.071 | 0.07 | 0.069 | 0.067 | 0.066 | 0.065 | 0.064
| 20 | 0.071 | 0.07 | 0.068 | 0.067 | 0.066 | 0.064 | 0.063 | 0.062 | 0.061
| 20.5 | 0.065 | 0.064 | 0.063 | 0.062 | 0.061 | 0.059 | 0.058 | 0.057 | 0.056
| 21 | 0.06 | 0.059 | 0.057 | 0.056 | 0.056 | 0.054 | 0.053 | 0.052 | 0.051
| 21.5 | 0.054 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046
| 22 | 0.049 | 0.049 | 0.047 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.043
| 22.5 | 0.045 | 0.045 | 0.043 | 0.043 | 0.042 | 0.041 | 0.04 | 0.04 | 0.039
| 23 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.038 | 0.037 | 0.036 | 0.036
| 23.5 | 0.038 | 0.037 | 0.036 | 0.036 | 0.035 | 0.034 | 0.033 | 0.033 | 0.032
| 24 | 0.035 | 0.034 | 0.033 | 0.033 | 0.032 | 0.031 | 0.031 | 0.03 | 0.03
| 24.5 | 0.032 | 0.032 | 0.031 | 0.03 | 0.03 | 0.029 | 0.028 | 0.028 | 0.027
| 25 | 0.03 | 0.029 | 0.028 | 0.028 | 0.028 | 0.027 | 0.026 | 0.026 | 0.025
| 25.5 | 0.027 | 0.027 | 0.026 | 0.026 | 0.025 | 0.025 | 0.024 | 0.024 | 0.023
| 26 | 0.025 | 0.025 | 0.024 | 0.024 | 0.024 | 0.023 | 0.023 | 0.022 | 0.022