## Sheet1
PROPERTIES
General
Name | Nordex N163/5.X Class B 108m 3,99MW
Manufacturer | Nordex
Hub Height | 108
Power
Rated Power | 3990
Peak Power | 3990
Power Regulation Type | Pitch
Voltage | 750
Rotor
Rotor diameter | 163
Number of blades | 3
Rated RPM | 11.8
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 26
Restart Wind Speed | 25.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 45
High Temperature Restart | 40
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | B
Values
Certification | IEC 3rd Edition
Vave | 6.5-8
Vref | 38.8-40.3
Design TI | 0.16

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 31 | 33 | 35 | 37 | 40 | 42 | 44 | 46 | 49
| 3.5 | 126 | 130 | 134 | 139 | 143 | 148 | 152 | 156 | 161
| 4 | 253 | 260 | 267 | 275 | 282 | 289 | 296 | 304 | 311
| 4.5 | 410 | 421 | 432 | 442 | 453 | 464 | 475 | 486 | 497
| 5 | 598 | 613 | 628 | 643 | 658 | 673 | 688 | 703 | 719
| 5.5 | 821 | 841 | 861 | 882 | 902 | 922 | 942 | 962 | 982
| 6 | 1080 | 1106 | 1132 | 1158 | 1184 | 1210 | 1236 | 1262 | 1288
| 6.5 | 1348 | 1380 | 1412 | 1444 | 1476 | 1508 | 1540 | 1572 | 1605
| 7 | 1608 | 1646 | 1684 | 1722 | 1760 | 1797 | 1835 | 1873 | 1911
| 7.5 | 1848 | 1891 | 1935 | 1978 | 2021 | 2064 | 2108 | 2151 | 2194
| 8 | 2071 | 2119 | 2167 | 2216 | 2264 | 2312 | 2360 | 2409 | 2457
| 8.5 | 2279 | 2332 | 2385 | 2438 | 2491 | 2544 | 2597 | 2650 | 2703
| 9 | 2477 | 2535 | 2592 | 2650 | 2707 | 2764 | 2822 | 2879 | 2936
| 9.5 | 2671 | 2733 | 2795 | 2857 | 2918 | 2980 | 3042 | 3103 | 3165
| 10 | 2863 | 2929 | 2995 | 3061 | 3127 | 3193 | 3259 | 3326 | 3390
| 10.5 | 3046 | 3117 | 3187 | 3256 | 3327 | 3398 | 3464 | 3529 | 3585
| 11 | 3222 | 3296 | 3370 | 3445 | 3514 | 3581 | 3636 | 3689 | 3733
| 11.5 | 3394 | 3473 | 3543 | 3612 | 3669 | 3724 | 3769 | 3811 | 3845
| 12 | 3556 | 3627 | 3686 | 3743 | 3788 | 3832 | 3866 | 3898 | 3922
| 12.5 | 3688 | 3747 | 3795 | 3841 | 3876 | 3909 | 3933 | 3955 | 3969
| 13 | 3790 | 3837 | 3874 | 3909 | 3934 | 3958 | 3972 | 3984 | 3988
| 13.5 | 3866 | 3903 | 3930 | 3955 | 3970 | 3983 | 3988 | 3990 | 3990
| 14 | 3923 | 3949 | 3966 | 3981 | 3987 | 3990 | 3990 | 3990 | 3990
| 14.5 | 3962 | 3979 | 3985 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990
| 15 | 3983 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990
| 15.5 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990
| 16 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990
| 16.5 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990
| 17 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990
| 17.5 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990
| 18 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990
| 18.5 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990
| 19 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990
| 19.5 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990
| 20 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990
| 20.5 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990
| 21 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990
| 21.5 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990
| 22 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990
| 22.5 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990
| 23 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990
| 23.5 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990
| 24 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990
| 24.5 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990
| 25 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990 | 3990
| 25.5 | 3987 | 3987 | 3987 | 3987 | 3987 | 3987 | 3987 | 3987 | 3987
| 26 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764
| 3.5 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208
| 4 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819
| 4.5 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639
| 5 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875
| 5.5 | 0.55347 | 0.55347 | 0.55347 | 0.55347 | 0.55347 | 0.55347 | 0.55347 | 0.55347 | 0.55347
| 6 | 0.52569 | 0.52569 | 0.52569 | 0.52569 | 0.52569 | 0.52569 | 0.52569 | 0.52569 | 0.52569
| 6.5 | 0.49097 | 0.49097 | 0.49097 | 0.49097 | 0.49097 | 0.49097 | 0.49097 | 0.49097 | 0.49097
| 7 | 0.45278 | 0.45278 | 0.45278 | 0.45278 | 0.45278 | 0.45278 | 0.45278 | 0.45278 | 0.45278
| 7.5 | 0.41319 | 0.41319 | 0.41319 | 0.41319 | 0.41319 | 0.41319 | 0.41319 | 0.41319 | 0.41319
| 8 | 0.37361 | 0.37361 | 0.37361 | 0.37361 | 0.37361 | 0.37361 | 0.37361 | 0.37361 | 0.37361
| 8.5 | 0.33472 | 0.33472 | 0.33472 | 0.33472 | 0.33472 | 0.33472 | 0.33472 | 0.33472 | 0.33472
| 9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
| 9.5 | 0.26944 | 0.26944 | 0.26944 | 0.26944 | 0.26944 | 0.26944 | 0.26944 | 0.26944 | 0.26875
| 10 | 0.24375 | 0.24375 | 0.24375 | 0.24375 | 0.24306 | 0.24306 | 0.24306 | 0.24236 | 0.24167
| 10.5 | 0.22083 | 0.22083 | 0.22083 | 0.22083 | 0.22014 | 0.21944 | 0.21875 | 0.21806 | 0.21736
| 11 | 0.20139 | 0.20069 | 0.20069 | 0.2 | 0.19931 | 0.19861 | 0.19722 | 0.19653 | 0.19514
| 11.5 | 0.18333 | 0.18264 | 0.18194 | 0.18125 | 0.18056 | 0.17986 | 0.17847 | 0.17708 | 0.17639
| 12 | 0.16736 | 0.16667 | 0.16597 | 0.16458 | 0.16389 | 0.1625 | 0.16111 | 0.16042 | 0.15903
| 12.5 | 0.15278 | 0.15208 | 0.15069 | 0.15 | 0.14861 | 0.14722 | 0.14653 | 0.14514 | 0.14375
| 13 | 0.13958 | 0.13889 | 0.1375 | 0.13681 | 0.13542 | 0.13403 | 0.13264 | 0.13125 | 0.12986
| 13.5 | 0.12778 | 0.12708 | 0.12569 | 0.12431 | 0.12292 | 0.12153 | 0.12014 | 0.11875 | 0.11736
| 14 | 0.11736 | 0.11597 | 0.11458 | 0.11389 | 0.1125 | 0.11111 | 0.10972 | 0.10833 | 0.10625
| 14.5 | 0.10764 | 0.10625 | 0.10486 | 0.10347 | 0.10208 | 0.10139 | 0.099306 | 0.097917 | 0.096528
| 15 | 0.098611 | 0.097222 | 0.095833 | 0.095139 | 0.09375 | 0.092361 | 0.090278 | 0.088889 | 0.0875
| 15.5 | 0.090972 | 0.089583 | 0.088194 | 0.086806 | 0.085417 | 0.084028 | 0.082639 | 0.08125 | 0.079167
| 16 | 0.083333 | 0.081944 | 0.080556 | 0.079167 | 0.077778 | 0.076389 | 0.075 | 0.073611 | 0.072222
| 16.5 | 0.077083 | 0.075694 | 0.074306 | 0.072917 | 0.071528 | 0.070139 | 0.099 | 0.097 | 0.095
| 17 | 0.071528 | 0.070139 | 0.099 | 0.097 | 0.095 | 0.093 | 0.091 | 0.09 | 0.088
| 17.5 | 0.095 | 0.093 | 0.092 | 0.09 | 0.088 | 0.086 | 0.085 | 0.083 | 0.082
| 18 | 0.089 | 0.087 | 0.085 | 0.084 | 0.082 | 0.08 | 0.079 | 0.078 | 0.076
| 18.5 | 0.084 | 0.082 | 0.08 | 0.079 | 0.077 | 0.076 | 0.074 | 0.073 | 0.072
| 19 | 0.079 | 0.077 | 0.076 | 0.074 | 0.073 | 0.071 | 0.07 | 0.069 | 0.068
| 19.5 | 0.075 | 0.073 | 0.072 | 0.07 | 0.069 | 0.068 | 0.067 | 0.065 | 0.064
| 20 | 0.071 | 0.07 | 0.069 | 0.067 | 0.066 | 0.065 | 0.064 | 0.062 | 0.061
| 20.5 | 0.065 | 0.064 | 0.063 | 0.062 | 0.061 | 0.06 | 0.059 | 0.057 | 0.056
| 21 | 0.06 | 0.059 | 0.058 | 0.056 | 0.056 | 0.055 | 0.054 | 0.052 | 0.051
| 21.5 | 0.054 | 0.053 | 0.053 | 0.051 | 0.05 | 0.05 | 0.049 | 0.047 | 0.046
| 22 | 0.049 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.045 | 0.043 | 0.043
| 22.5 | 0.045 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.041 | 0.04 | 0.039
| 23 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.038 | 0.038 | 0.036 | 0.036
| 23.5 | 0.038 | 0.037 | 0.037 | 0.036 | 0.035 | 0.035 | 0.034 | 0.033 | 0.032
| 24 | 0.035 | 0.034 | 0.034 | 0.033 | 0.032 | 0.032 | 0.031 | 0.03 | 0.03
| 24.5 | 0.032 | 0.032 | 0.031 | 0.03 | 0.03 | 0.029 | 0.029 | 0.028 | 0.027
| 25 | 0.03 | 0.029 | 0.029 | 0.028 | 0.028 | 0.027 | 0.027 | 0.026 | 0.025
| 25.5 | 0.027 | 0.027 | 0.027 | 0.026 | 0.025 | 0.025 | 0.025 | 0.024 | 0.023
| 26 | 0.025 | 0.025 | 0.025 | 0.024 | 0.024 | 0.023 | 0.023 | 0.022 | 0.022