## Sheet1
PROPERTIES
General
Name | Nordex N163/5.X Class B 3,7MW
Manufacturer | Nordex
Hub Height | 118 | 120 | 148 | 159 | 164
Power
Rated Power | 3700
Peak Power | 3700
Power Regulation Type | Pitch
Voltage | 750
Rotor
Rotor diameter | 163
Number of blades | 3
Rated RPM | 11.8
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 26
Restart Wind Speed | 25.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 45
High Temperature Restart | 40
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | B
Values
Certification | IEC 3rd Edition
Vave | 6.5-8
Vref | 38.8-40.3
Design TI | 0.16

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 37 | 39 | 41 | 44 | 46 | 48 | 50 | 53 | 55
| 3.5 | 133 | 137 | 142 | 146 | 151 | 155 | 159 | 164 | 168
| 4 | 261 | 268 | 276 | 283 | 290 | 298 | 305 | 312 | 320
| 4.5 | 420 | 431 | 441 | 452 | 463 | 474 | 485 | 496 | 507
| 5 | 609 | 624 | 639 | 655 | 670 | 685 | 700 | 716 | 731
| 5.5 | 834 | 854 | 874 | 895 | 915 | 935 | 956 | 976 | 996
| 6 | 1088 | 1114 | 1140 | 1166 | 1192 | 1218 | 1244 | 1270 | 1296
| 6.5 | 1345 | 1377 | 1409 | 1440 | 1472 | 1504 | 1536 | 1568 | 1599
| 7 | 1589 | 1626 | 1664 | 1701 | 1738 | 1776 | 1813 | 1850 | 1887
| 7.5 | 1814 | 1856 | 1899 | 1941 | 1983 | 2026 | 2068 | 2110 | 2152
| 8 | 2022 | 2069 | 2116 | 2163 | 2210 | 2257 | 2304 | 2351 | 2398
| 8.5 | 2218 | 2269 | 2321 | 2372 | 2423 | 2474 | 2526 | 2577 | 2628
| 9 | 2406 | 2462 | 2517 | 2572 | 2628 | 2683 | 2739 | 2794 | 2849
| 9.5 | 2591 | 2651 | 2710 | 2770 | 2830 | 2889 | 2949 | 3008 | 3068
| 10 | 2772 | 2836 | 2900 | 2963 | 3027 | 3091 | 3153 | 3214 | 3271
| 10.5 | 2944 | 3011 | 3079 | 3147 | 3212 | 3275 | 3332 | 3380 | 3427
| 11 | 3110 | 3182 | 3250 | 3314 | 3372 | 3422 | 3468 | 3507 | 3543
| 11.5 | 3270 | 3336 | 3395 | 3447 | 3494 | 3534 | 3569 | 3598 | 3625
| 12 | 3403 | 3458 | 3505 | 3548 | 3584 | 3614 | 3639 | 3659 | 3676
| 12.5 | 3505 | 3549 | 3586 | 3618 | 3644 | 3665 | 3681 | 3691 | 3699
| 13 | 3581 | 3614 | 3641 | 3664 | 3680 | 3691 | 3698 | 3700 | 3700
| 13.5 | 3636 | 3660 | 3677 | 3690 | 3697 | 3699 | 3700 | 3700 | 3700
| 14 | 3673 | 3688 | 3696 | 3699 | 3700 | 3700 | 3700 | 3700 | 3700
| 14.5 | 3694 | 3699 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700
| 15 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700
| 15.5 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700
| 16 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700
| 16.5 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700
| 17 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700
| 17.5 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700
| 18 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700
| 18.5 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700
| 19 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700
| 19.5 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700
| 20 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700
| 20.5 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700
| 21 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700
| 21.5 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700
| 22 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700
| 22.5 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700
| 23 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700
| 23.5 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700
| 24 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700
| 24.5 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700
| 25 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700
| 25.5 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700
| 26 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700 | 3700

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764
| 3.5 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208
| 4 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819
| 4.5 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639
| 5 | 0.56806 | 0.56806 | 0.56806 | 0.56806 | 0.56806 | 0.56806 | 0.56806 | 0.56806 | 0.56806
| 5.5 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861 | 0.54861
| 6 | 0.51667 | 0.51667 | 0.51667 | 0.51667 | 0.51667 | 0.51667 | 0.51667 | 0.51667 | 0.51667
| 6.5 | 0.47986 | 0.47986 | 0.47986 | 0.47986 | 0.47986 | 0.47986 | 0.47986 | 0.47986 | 0.47986
| 7 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028
| 7.5 | 0.39931 | 0.39931 | 0.39931 | 0.39931 | 0.39931 | 0.39931 | 0.39931 | 0.39931 | 0.39931
| 8 | 0.35903 | 0.35903 | 0.35903 | 0.35903 | 0.35903 | 0.35903 | 0.35903 | 0.35903 | 0.35903
| 8.5 | 0.32014 | 0.32014 | 0.32014 | 0.32014 | 0.32014 | 0.32014 | 0.32014 | 0.32014 | 0.32014
| 9 | 0.28681 | 0.28681 | 0.28681 | 0.28681 | 0.28681 | 0.28681 | 0.28681 | 0.28611 | 0.28611
| 9.5 | 0.25764 | 0.25764 | 0.25764 | 0.25764 | 0.25764 | 0.25764 | 0.25694 | 0.25625 | 0.25625
| 10 | 0.23264 | 0.23264 | 0.23264 | 0.23264 | 0.23194 | 0.23125 | 0.23056 | 0.22986 | 0.22917
| 10.5 | 0.21111 | 0.21042 | 0.21042 | 0.20972 | 0.20903 | 0.20833 | 0.20764 | 0.20625 | 0.20556
| 11 | 0.19167 | 0.19097 | 0.19028 | 0.18958 | 0.18889 | 0.18819 | 0.18681 | 0.18542 | 0.18472
| 11.5 | 0.17431 | 0.17361 | 0.17292 | 0.17153 | 0.17083 | 0.16944 | 0.16806 | 0.16736 | 0.16597
| 12 | 0.15833 | 0.15764 | 0.15694 | 0.15556 | 0.15417 | 0.15347 | 0.15208 | 0.15069 | 0.14931
| 12.5 | 0.14444 | 0.14375 | 0.14236 | 0.14097 | 0.14028 | 0.13889 | 0.1375 | 0.13611 | 0.13472
| 13 | 0.13194 | 0.13056 | 0.12986 | 0.12847 | 0.12708 | 0.12569 | 0.12431 | 0.12292 | 0.12153
| 13.5 | 0.12014 | 0.11944 | 0.11806 | 0.11667 | 0.11528 | 0.11389 | 0.1125 | 0.11111 | 0.10972
| 14 | 0.11042 | 0.10903 | 0.10764 | 0.10625 | 0.10486 | 0.10347 | 0.10208 | 0.10069 | 0.099306
| 14.5 | 0.10069 | 0.099306 | 0.097917 | 0.096528 | 0.095139 | 0.09375 | 0.092361 | 0.090972 | 0.089583
| 15 | 0.092361 | 0.090972 | 0.089583 | 0.088194 | 0.086806 | 0.085417 | 0.084028 | 0.082639 | 0.080556
| 15.5 | 0.084722 | 0.083333 | 0.081944 | 0.080556 | 0.079167 | 0.077778 | 0.076389 | 0.075 | 0.073611
| 16 | 0.077778 | 0.076389 | 0.075 | 0.073611 | 0.072222 | 0.070833 | 0.069444 | 0.098 | 0.096
| 16.5 | 0.071528 | 0.070139 | 0.099 | 0.097 | 0.095 | 0.093 | 0.091 | 0.09 | 0.088
| 17 | 0.095 | 0.093 | 0.091 | 0.089 | 0.088 | 0.086 | 0.084 | 0.083 | 0.081
| 17.5 | 0.088 | 0.086 | 0.085 | 0.083 | 0.081 | 0.08 | 0.078 | 0.077 | 0.075
| 18 | 0.082 | 0.081 | 0.079 | 0.077 | 0.076 | 0.074 | 0.073 | 0.072 | 0.071
| 18.5 | 0.077 | 0.076 | 0.074 | 0.073 | 0.071 | 0.07 | 0.069 | 0.067 | 0.066
| 19 | 0.073 | 0.071 | 0.07 | 0.069 | 0.067 | 0.066 | 0.065 | 0.064 | 0.063
| 19.5 | 0.069 | 0.068 | 0.067 | 0.065 | 0.064 | 0.063 | 0.062 | 0.061 | 0.06
| 20 | 0.066 | 0.065 | 0.064 | 0.062 | 0.061 | 0.06 | 0.059 | 0.058 | 0.057
| 20.5 | 0.061 | 0.06 | 0.059 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053 | 0.052
| 21 | 0.056 | 0.055 | 0.054 | 0.052 | 0.051 | 0.05 | 0.05 | 0.049 | 0.048
| 21.5 | 0.05 | 0.05 | 0.049 | 0.047 | 0.046 | 0.046 | 0.045 | 0.044 | 0.043
| 22 | 0.046 | 0.045 | 0.045 | 0.043 | 0.043 | 0.042 | 0.041 | 0.04 | 0.04
| 22.5 | 0.042 | 0.041 | 0.041 | 0.04 | 0.039 | 0.038 | 0.038 | 0.037 | 0.036
| 23 | 0.039 | 0.038 | 0.038 | 0.036 | 0.036 | 0.035 | 0.035 | 0.034 | 0.033
| 23.5 | 0.035 | 0.035 | 0.034 | 0.033 | 0.032 | 0.032 | 0.031 | 0.031 | 0.03
| 24 | 0.032 | 0.032 | 0.031 | 0.03 | 0.03 | 0.029 | 0.029 | 0.028 | 0.028
| 24.5 | 0.03 | 0.029 | 0.029 | 0.028 | 0.027 | 0.027 | 0.027 | 0.026 | 0.026
| 25 | 0.028 | 0.027 | 0.027 | 0.026 | 0.025 | 0.025 | 0.025 | 0.024 | 0.024
| 25.5 | 0.025 | 0.025 | 0.025 | 0.024 | 0.023 | 0.023 | 0.023 | 0.022 | 0.022
| 26 | 0.024 | 0.023 | 0.023 | 0.022 | 0.022 | 0.021 | 0.021 | 0.021 | 0.02