## Sheet1
PROPERTIES
General
Name | Nordex N163/5.X Class B 3,45MW
Manufacturer | Nordex
Hub Height | 118 | 148 | 159 | 164
Power
Rated Power | 3450
Peak Power | 3450
Power Regulation Type | Pitch
Voltage | 750
Rotor
Rotor diameter | 163
Number of blades | 3
Rated RPM | 11.8
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 26
Restart Wind Speed | 25.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 45
High Temperature Restart | 40
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | B
Values
Certification | IEC 3rd Edition
Vave | 6.5-8
Vref | 38.8-40.3
Design TI | 0.16

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 37 | 39 | 41 | 44 | 46 | 48 | 51 | 53 | 55
| 3.5 | 133 | 137 | 142 | 146 | 151 | 155 | 159 | 164 | 168
| 4 | 261 | 268 | 276 | 283 | 290 | 298 | 305 | 312 | 320
| 4.5 | 420 | 431 | 442 | 452 | 463 | 474 | 485 | 496 | 507
| 5 | 609 | 624 | 639 | 655 | 670 | 685 | 700 | 716 | 731
| 5.5 | 833 | 854 | 874 | 894 | 915 | 935 | 955 | 975 | 996
| 6 | 1079 | 1105 | 1131 | 1157 | 1183 | 1209 | 1234 | 1260 | 1286
| 6.5 | 1324 | 1355 | 1386 | 1418 | 1449 | 1480 | 1512 | 1543 | 1574
| 7 | 1551 | 1588 | 1624 | 1661 | 1697 | 1733 | 1770 | 1806 | 1843
| 7.5 | 1762 | 1803 | 1844 | 1885 | 1926 | 1967 | 2008 | 2049 | 2090
| 8 | 1956 | 2002 | 2047 | 2093 | 2138 | 2184 | 2229 | 2275 | 2320
| 8.5 | 2140 | 2190 | 2239 | 2289 | 2339 | 2388 | 2438 | 2487 | 2537
| 9 | 2319 | 2373 | 2426 | 2480 | 2533 | 2587 | 2640 | 2694 | 2747
| 9.5 | 2495 | 2553 | 2610 | 2668 | 2725 | 2783 | 2840 | 2897 | 2953
| 10 | 2664 | 2725 | 2787 | 2848 | 2910 | 2969 | 3027 | 3079 | 3124
| 10.5 | 2826 | 2891 | 2956 | 3018 | 3078 | 3129 | 3176 | 3218 | 3253
| 11 | 2985 | 3048 | 3110 | 3162 | 3211 | 3252 | 3289 | 3320 | 3346
| 11.5 | 3126 | 3179 | 3229 | 3271 | 3310 | 3341 | 3369 | 3391 | 3408
| 12 | 3235 | 3278 | 3318 | 3350 | 3379 | 3401 | 3420 | 3433 | 3440
| 12.5 | 3317 | 3349 | 3380 | 3402 | 3422 | 3435 | 3444 | 3449 | 3450
| 13 | 3376 | 3399 | 3421 | 3434 | 3445 | 3449 | 3450 | 3450 | 3450
| 13.5 | 3417 | 3431 | 3444 | 3448 | 3450 | 3450 | 3450 | 3450 | 3450
| 14 | 3442 | 3447 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 14.5 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 15 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 15.5 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 16 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 16.5 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 17 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 17.5 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 18 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 18.5 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 19 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 19.5 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 20 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 20.5 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 21 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 21.5 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 22 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 22.5 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 23 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 23.5 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 24 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 24.5 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 25 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 25.5 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 26 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764
| 3.5 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208
| 4 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819
| 4.5 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639
| 5 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736
| 5.5 | 0.54375 | 0.54375 | 0.54375 | 0.54375 | 0.54375 | 0.54375 | 0.54375 | 0.54375 | 0.54375
| 6 | 0.50903 | 0.50903 | 0.50903 | 0.50903 | 0.50903 | 0.50903 | 0.50903 | 0.50903 | 0.50903
| 6.5 | 0.46944 | 0.46944 | 0.46944 | 0.46944 | 0.46944 | 0.46944 | 0.46944 | 0.46944 | 0.46944
| 7 | 0.42847 | 0.42847 | 0.42847 | 0.42847 | 0.42847 | 0.42847 | 0.42847 | 0.42847 | 0.42847
| 7.5 | 0.38681 | 0.38681 | 0.38681 | 0.38681 | 0.38681 | 0.38681 | 0.38681 | 0.38681 | 0.38681
| 8 | 0.34514 | 0.34514 | 0.34514 | 0.34514 | 0.34514 | 0.34514 | 0.34514 | 0.34514 | 0.34514
| 8.5 | 0.30694 | 0.30694 | 0.30694 | 0.30694 | 0.30694 | 0.30694 | 0.30694 | 0.30694 | 0.30694
| 9 | 0.27431 | 0.27431 | 0.27431 | 0.27431 | 0.27431 | 0.27431 | 0.27431 | 0.27361 | 0.27361
| 9.5 | 0.24653 | 0.24653 | 0.24653 | 0.24653 | 0.24653 | 0.24583 | 0.24514 | 0.24514 | 0.24375
| 10 | 0.22222 | 0.22222 | 0.22222 | 0.22153 | 0.22153 | 0.22083 | 0.22014 | 0.21875 | 0.21806
| 10.5 | 0.20139 | 0.20139 | 0.20069 | 0.2 | 0.19931 | 0.19792 | 0.19722 | 0.19653 | 0.19514
| 11 | 0.18264 | 0.18194 | 0.18125 | 0.18056 | 0.17917 | 0.17847 | 0.17708 | 0.17569 | 0.175
| 11.5 | 0.16597 | 0.16458 | 0.16389 | 0.16319 | 0.16181 | 0.16042 | 0.15972 | 0.15833 | 0.15694
| 12 | 0.15069 | 0.14931 | 0.14861 | 0.14722 | 0.14653 | 0.14514 | 0.14375 | 0.14236 | 0.14097
| 12.5 | 0.13681 | 0.13611 | 0.13472 | 0.13333 | 0.13264 | 0.13125 | 0.12986 | 0.12778 | 0.12639
| 13 | 0.125 | 0.12361 | 0.12222 | 0.12153 | 0.12014 | 0.11875 | 0.11736 | 0.11528 | 0.11389
| 13.5 | 0.11389 | 0.1125 | 0.11111 | 0.10972 | 0.10903 | 0.10694 | 0.10556 | 0.10417 | 0.10278
| 14 | 0.10417 | 0.10278 | 0.10139 | 0.1 | 0.098611 | 0.097222 | 0.095833 | 0.094444 | 0.092361
| 14.5 | 0.095139 | 0.09375 | 0.092361 | 0.090972 | 0.089583 | 0.088194 | 0.086806 | 0.084722 | 0.083333
| 15 | 0.086806 | 0.085417 | 0.084028 | 0.082639 | 0.08125 | 0.079861 | 0.078472 | 0.077083 | 0.075694
| 15.5 | 0.079861 | 0.078472 | 0.077083 | 0.075694 | 0.073611 | 0.072222 | 0.070833 | 0.069444 | 0.099
| 16 | 0.072917 | 0.071528 | 0.070139 | 0.099 | 0.097 | 0.095 | 0.093 | 0.092 | 0.09
| 16.5 | 0.096 | 0.094 | 0.093 | 0.091 | 0.089 | 0.087 | 0.085 | 0.084 | 0.082
| 17 | 0.089 | 0.087 | 0.085 | 0.084 | 0.082 | 0.08 | 0.079 | 0.077 | 0.076
| 17.5 | 0.083 | 0.081 | 0.079 | 0.078 | 0.076 | 0.075 | 0.073 | 0.072 | 0.071
| 18 | 0.077 | 0.075 | 0.074 | 0.072 | 0.071 | 0.07 | 0.068 | 0.067 | 0.066
| 18.5 | 0.072 | 0.071 | 0.069 | 0.068 | 0.067 | 0.066 | 0.064 | 0.063 | 0.062
| 19 | 0.068 | 0.067 | 0.066 | 0.064 | 0.063 | 0.062 | 0.061 | 0.06 | 0.059
| 19.5 | 0.065 | 0.064 | 0.062 | 0.061 | 0.06 | 0.059 | 0.058 | 0.057 | 0.056
| 20 | 0.062 | 0.061 | 0.06 | 0.058 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053
| 20.5 | 0.057 | 0.056 | 0.055 | 0.053 | 0.052 | 0.052 | 0.051 | 0.05 | 0.049
| 21 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.045
| 21.5 | 0.047 | 0.046 | 0.046 | 0.044 | 0.043 | 0.043 | 0.042 | 0.041 | 0.04
| 22 | 0.043 | 0.043 | 0.042 | 0.04 | 0.04 | 0.039 | 0.038 | 0.038 | 0.037
| 22.5 | 0.04 | 0.039 | 0.038 | 0.037 | 0.036 | 0.036 | 0.035 | 0.034 | 0.034
| 23 | 0.036 | 0.036 | 0.035 | 0.034 | 0.033 | 0.033 | 0.032 | 0.032 | 0.031
| 23.5 | 0.033 | 0.032 | 0.032 | 0.031 | 0.03 | 0.03 | 0.029 | 0.029 | 0.028
| 24 | 0.03 | 0.03 | 0.029 | 0.028 | 0.028 | 0.027 | 0.027 | 0.026 | 0.026
| 24.5 | 0.028 | 0.027 | 0.027 | 0.026 | 0.026 | 0.025 | 0.025 | 0.024 | 0.024
| 25 | 0.026 | 0.025 | 0.025 | 0.024 | 0.024 | 0.023 | 0.023 | 0.023 | 0.022
| 25.5 | 0.024 | 0.023 | 0.023 | 0.022 | 0.022 | 0.022 | 0.021 | 0.021 | 0.02
| 26 | 0.022 | 0.022 | 0.021 | 0.021 | 0.02 | 0.02 | 0.02 | 0.019 | 0.019