## Sheet1
PROPERTIES
General
Name | Nordex N163/5.X Class B 108m 3,45MW
Manufacturer | Nordex
Hub Height | 108
Power
Rated Power | 3450
Peak Power | 3450
Power Regulation Type | Pitch
Voltage | 750
Rotor
Rotor diameter | 163
Number of blades | 3
Rated RPM | 11.8
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 26
Restart Wind Speed | 25.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 45
High Temperature Restart | 40
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | B
Values
Certification | IEC 3rd Edition
Vave | 6.5-8
Vref | 38.8-40.3
Design TI | 0.16

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 31 | 33 | 35 | 37 | 40 | 42 | 44 | 46 | 49
| 3.5 | 126 | 130 | 134 | 139 | 143 | 148 | 152 | 156 | 161
| 4 | 253 | 260 | 267 | 274 | 282 | 289 | 296 | 304 | 311
| 4.5 | 410 | 421 | 432 | 442 | 453 | 464 | 475 | 486 | 497
| 5 | 598 | 613 | 628 | 643 | 658 | 673 | 688 | 703 | 719
| 5.5 | 820 | 840 | 861 | 881 | 901 | 921 | 941 | 961 | 981
| 6 | 1065 | 1090 | 1116 | 1142 | 1167 | 1193 | 1219 | 1244 | 1270
| 6.5 | 1307 | 1338 | 1369 | 1401 | 1432 | 1463 | 1494 | 1525 | 1556
| 7 | 1533 | 1570 | 1606 | 1642 | 1678 | 1715 | 1751 | 1787 | 1823
| 7.5 | 1743 | 1784 | 1824 | 1865 | 1906 | 1947 | 1988 | 2029 | 2070
| 8 | 1936 | 1982 | 2027 | 2072 | 2118 | 2163 | 2208 | 2253 | 2299
| 8.5 | 2119 | 2169 | 2218 | 2268 | 2317 | 2366 | 2416 | 2465 | 2514
| 9 | 2298 | 2351 | 2404 | 2458 | 2511 | 2564 | 2618 | 2671 | 2725
| 9.5 | 2473 | 2531 | 2588 | 2645 | 2703 | 2760 | 2818 | 2875 | 2930
| 10 | 2642 | 2703 | 2764 | 2825 | 2887 | 2947 | 3005 | 3061 | 3106
| 10.5 | 2803 | 2868 | 2933 | 2996 | 3056 | 3112 | 3159 | 3204 | 3240
| 11 | 2961 | 3027 | 3089 | 3144 | 3193 | 3238 | 3275 | 3311 | 3336
| 11.5 | 3105 | 3162 | 3212 | 3257 | 3296 | 3331 | 3359 | 3385 | 3402
| 12 | 3218 | 3264 | 3305 | 3340 | 3369 | 3395 | 3413 | 3430 | 3438
| 12.5 | 3303 | 3339 | 3370 | 3396 | 3416 | 3432 | 3441 | 3449 | 3450
| 13 | 3366 | 3392 | 3414 | 3430 | 3441 | 3448 | 3449 | 3450 | 3450
| 13.5 | 3410 | 3427 | 3440 | 3447 | 3449 | 3450 | 3450 | 3450 | 3450
| 14 | 3437 | 3446 | 3449 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 14.5 | 3449 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 15 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 15.5 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 16 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 16.5 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 17 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 17.5 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 18 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 18.5 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 19 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 19.5 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 20 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 20.5 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 21 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 21.5 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 22 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 22.5 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 23 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 23.5 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 24 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 24.5 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 25 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 25.5 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| 26 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764
| 3.5 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208
| 4 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819
| 4.5 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639
| 5 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736 | 0.56736
| 5.5 | 0.54375 | 0.54375 | 0.54375 | 0.54375 | 0.54375 | 0.54375 | 0.54375 | 0.54375 | 0.54375
| 6 | 0.50903 | 0.50903 | 0.50903 | 0.50903 | 0.50903 | 0.50903 | 0.50903 | 0.50903 | 0.50903
| 6.5 | 0.46944 | 0.46944 | 0.46944 | 0.46944 | 0.46944 | 0.46944 | 0.46944 | 0.46944 | 0.46944
| 7 | 0.42847 | 0.42847 | 0.42847 | 0.42847 | 0.42847 | 0.42847 | 0.42847 | 0.42847 | 0.42847
| 7.5 | 0.38681 | 0.38681 | 0.38681 | 0.38681 | 0.38681 | 0.38681 | 0.38681 | 0.38681 | 0.38681
| 8 | 0.34514 | 0.34514 | 0.34514 | 0.34514 | 0.34514 | 0.34514 | 0.34514 | 0.34514 | 0.34514
| 8.5 | 0.30694 | 0.30694 | 0.30694 | 0.30694 | 0.30694 | 0.30694 | 0.30694 | 0.30694 | 0.30694
| 9 | 0.27431 | 0.27431 | 0.27431 | 0.27431 | 0.27431 | 0.27431 | 0.27431 | 0.27431 | 0.27361
| 9.5 | 0.24653 | 0.24653 | 0.24653 | 0.24653 | 0.24653 | 0.24583 | 0.24583 | 0.24514 | 0.24444
| 10 | 0.22222 | 0.22222 | 0.22222 | 0.22222 | 0.22153 | 0.22083 | 0.22014 | 0.21944 | 0.21806
| 10.5 | 0.20139 | 0.20139 | 0.20069 | 0.2 | 0.19931 | 0.19861 | 0.19792 | 0.19653 | 0.19514
| 11 | 0.18264 | 0.18194 | 0.18125 | 0.18056 | 0.17986 | 0.17847 | 0.17778 | 0.17639 | 0.175
| 11.5 | 0.16597 | 0.16528 | 0.16458 | 0.16319 | 0.1625 | 0.16111 | 0.15972 | 0.15833 | 0.15694
| 12 | 0.15069 | 0.15 | 0.14861 | 0.14792 | 0.14653 | 0.14514 | 0.14375 | 0.14306 | 0.14097
| 12.5 | 0.1375 | 0.13611 | 0.13542 | 0.13403 | 0.13264 | 0.13125 | 0.12986 | 0.12847 | 0.12708
| 13 | 0.125 | 0.12431 | 0.12292 | 0.12153 | 0.12014 | 0.11875 | 0.11736 | 0.11597 | 0.11458
| 13.5 | 0.11458 | 0.11319 | 0.11181 | 0.11042 | 0.10903 | 0.10764 | 0.10625 | 0.10486 | 0.10347
| 14 | 0.10417 | 0.10278 | 0.10208 | 0.10069 | 0.099306 | 0.097917 | 0.096528 | 0.094444 | 0.093056
| 14.5 | 0.095139 | 0.09375 | 0.093056 | 0.091667 | 0.090278 | 0.088889 | 0.086806 | 0.085417 | 0.084028
| 15 | 0.0875 | 0.086111 | 0.084722 | 0.083333 | 0.081944 | 0.080556 | 0.079167 | 0.077083 | 0.075694
| 15.5 | 0.079861 | 0.078472 | 0.077083 | 0.075694 | 0.074306 | 0.072917 | 0.071528 | 0.070139 | 0.099
| 16 | 0.072917 | 0.072222 | 0.070833 | 0.069444 | 0.098 | 0.096 | 0.094 | 0.092 | 0.09
| 16.5 | 0.097 | 0.095 | 0.093 | 0.091 | 0.089 | 0.088 | 0.086 | 0.084 | 0.083
| 17 | 0.09 | 0.088 | 0.086 | 0.084 | 0.082 | 0.081 | 0.079 | 0.078 | 0.077
| 17.5 | 0.083 | 0.081 | 0.08 | 0.078 | 0.077 | 0.075 | 0.074 | 0.072 | 0.071
| 18 | 0.078 | 0.076 | 0.074 | 0.073 | 0.072 | 0.07 | 0.069 | 0.068 | 0.066
| 18.5 | 0.073 | 0.071 | 0.07 | 0.068 | 0.067 | 0.066 | 0.065 | 0.064 | 0.063
| 19 | 0.069 | 0.067 | 0.066 | 0.065 | 0.064 | 0.062 | 0.061 | 0.06 | 0.059
| 19.5 | 0.065 | 0.064 | 0.063 | 0.062 | 0.06 | 0.059 | 0.058 | 0.057 | 0.056
| 20 | 0.062 | 0.061 | 0.06 | 0.059 | 0.058 | 0.057 | 0.056 | 0.055 | 0.054
| 20.5 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053 | 0.052 | 0.052 | 0.051 | 0.05
| 21 | 0.052 | 0.051 | 0.05 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045
| 21.5 | 0.047 | 0.046 | 0.046 | 0.045 | 0.044 | 0.043 | 0.043 | 0.042 | 0.041
| 22 | 0.043 | 0.043 | 0.042 | 0.041 | 0.04 | 0.04 | 0.039 | 0.038 | 0.038
| 22.5 | 0.04 | 0.039 | 0.038 | 0.038 | 0.037 | 0.036 | 0.036 | 0.035 | 0.034
| 23 | 0.036 | 0.036 | 0.035 | 0.035 | 0.034 | 0.033 | 0.033 | 0.032 | 0.032
| 23.5 | 0.033 | 0.032 | 0.032 | 0.031 | 0.031 | 0.03 | 0.03 | 0.029 | 0.029
| 24 | 0.03 | 0.03 | 0.029 | 0.029 | 0.028 | 0.028 | 0.027 | 0.027 | 0.026
| 24.5 | 0.028 | 0.027 | 0.027 | 0.027 | 0.026 | 0.026 | 0.025 | 0.025 | 0.024
| 25 | 0.026 | 0.025 | 0.025 | 0.025 | 0.024 | 0.024 | 0.023 | 0.023 | 0.023
| 25.5 | 0.024 | 0.023 | 0.023 | 0.023 | 0.022 | 0.022 | 0.022 | 0.021 | 0.021
| 26 | 0.022 | 0.022 | 0.021 | 0.021 | 0.021 | 0.02 | 0.02 | 0.02 | 0.019