## Sheet1
PROPERTIES
General
Name | Nordex N163/5.X Class B 108m 3,2MW
Manufacturer | Nordex
Hub Height | 108
Power
Rated Power | 3200
Peak Power | 3200
Power Regulation Type | Pitch
Voltage | 750
Rotor
Rotor diameter | 163
Number of blades | 3
Rated RPM | 11.8
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 26
Restart Wind Speed | 25.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 45
High Temperature Restart | 40
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | B
Values
Certification | IEC 3rd Edition
Vave | 6.5-8
Vref | 38.8-40.3
Design TI | 0.16

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 31 | 33 | 35 | 37 | 40 | 42 | 44 | 47 | 49
| 3.5 | 126 | 130 | 134 | 139 | 143 | 148 | 152 | 156 | 161
| 4 | 253 | 260 | 267 | 274 | 282 | 289 | 296 | 304 | 311
| 4.5 | 410 | 421 | 432 | 442 | 453 | 464 | 475 | 486 | 497
| 5 | 598 | 613 | 628 | 643 | 658 | 673 | 688 | 703 | 719
| 5.5 | 819 | 839 | 859 | 879 | 899 | 919 | 939 | 960 | 980
| 6 | 1053 | 1078 | 1104 | 1129 | 1155 | 1180 | 1205 | 1231 | 1256
| 6.5 | 1281 | 1311 | 1342 | 1372 | 1403 | 1433 | 1464 | 1494 | 1525
| 7 | 1490 | 1526 | 1561 | 1596 | 1631 | 1667 | 1702 | 1737 | 1772
| 7.5 | 1684 | 1723 | 1763 | 1803 | 1842 | 1882 | 1921 | 1961 | 2000
| 8 | 1864 | 1908 | 1952 | 1995 | 2039 | 2083 | 2126 | 2170 | 2213
| 8.5 | 2036 | 2084 | 2131 | 2179 | 2226 | 2274 | 2321 | 2369 | 2416
| 9 | 2205 | 2256 | 2308 | 2359 | 2410 | 2462 | 2513 | 2564 | 2616
| 9.5 | 2371 | 2426 | 2481 | 2536 | 2591 | 2647 | 2701 | 2754 | 2807
| 10 | 2528 | 2586 | 2645 | 2704 | 2761 | 2817 | 2867 | 2910 | 2953
| 10.5 | 2680 | 2743 | 2801 | 2859 | 2909 | 2954 | 2994 | 3028 | 3061
| 11 | 2825 | 2884 | 2934 | 2981 | 3020 | 3056 | 3087 | 3112 | 3136
| 11.5 | 2946 | 2994 | 3034 | 3071 | 3102 | 3128 | 3150 | 3166 | 3182
| 12 | 3037 | 3076 | 3106 | 3134 | 3155 | 3173 | 3186 | 3193 | 3200
| 12.5 | 3103 | 3133 | 3154 | 3173 | 3185 | 3194 | 3199 | 3200 | 3200
| 13 | 3151 | 3171 | 3184 | 3194 | 3199 | 3200 | 3200 | 3200 | 3200
| 13.5 | 3182 | 3194 | 3198 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 14 | 3197 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 14.5 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 15 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 15.5 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 16 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 16.5 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 17 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 17.5 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 18 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 18.5 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 19 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 19.5 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 20 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 20.5 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 21 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 21.5 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 22 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 22.5 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 23 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 23.5 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 24 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 24.5 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 25 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 25.5 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200
| 26 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200 | 3200

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764
| 3.5 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208
| 4 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819
| 4.5 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639
| 5 | 0.56319 | 0.56319 | 0.56319 | 0.56319 | 0.56319 | 0.56319 | 0.56319 | 0.56319 | 0.56319
| 5.5 | 0.53472 | 0.53472 | 0.53472 | 0.53472 | 0.53472 | 0.53472 | 0.53472 | 0.53472 | 0.53472
| 6 | 0.49722 | 0.49722 | 0.49722 | 0.49722 | 0.49722 | 0.49722 | 0.49722 | 0.49722 | 0.49722
| 6.5 | 0.45556 | 0.45556 | 0.45556 | 0.45556 | 0.45556 | 0.45556 | 0.45556 | 0.45556 | 0.45556
| 7 | 0.41319 | 0.41319 | 0.41319 | 0.41319 | 0.41319 | 0.41319 | 0.41319 | 0.41319 | 0.41319
| 7.5 | 0.37083 | 0.37083 | 0.37083 | 0.37083 | 0.37083 | 0.37083 | 0.37083 | 0.37083 | 0.37083
| 8 | 0.32986 | 0.32986 | 0.32986 | 0.32986 | 0.32986 | 0.32986 | 0.32986 | 0.32986 | 0.32986
| 8.5 | 0.29236 | 0.29236 | 0.29236 | 0.29236 | 0.29236 | 0.29236 | 0.29236 | 0.29236 | 0.29236
| 9 | 0.26111 | 0.26111 | 0.26111 | 0.26111 | 0.26111 | 0.26111 | 0.26111 | 0.26042 | 0.26042
| 9.5 | 0.23472 | 0.23472 | 0.23472 | 0.23472 | 0.23403 | 0.23403 | 0.23333 | 0.23264 | 0.23194
| 10 | 0.21181 | 0.21181 | 0.21111 | 0.21111 | 0.21042 | 0.20972 | 0.20903 | 0.20764 | 0.20694
| 10.5 | 0.19167 | 0.19097 | 0.19028 | 0.18958 | 0.18889 | 0.18819 | 0.18681 | 0.18611 | 0.18472
| 11 | 0.17361 | 0.17292 | 0.17222 | 0.17083 | 0.17014 | 0.16875 | 0.16806 | 0.16667 | 0.16528
| 11.5 | 0.15694 | 0.15625 | 0.15556 | 0.15417 | 0.15278 | 0.15208 | 0.15069 | 0.14931 | 0.14792
| 12 | 0.14236 | 0.14167 | 0.14028 | 0.13958 | 0.13819 | 0.13681 | 0.13542 | 0.13403 | 0.13264
| 12.5 | 0.12986 | 0.12847 | 0.12708 | 0.12639 | 0.125 | 0.12361 | 0.12222 | 0.12083 | 0.11944
| 13 | 0.11806 | 0.11667 | 0.11528 | 0.11458 | 0.11319 | 0.11181 | 0.11042 | 0.10833 | 0.10694
| 13.5 | 0.10764 | 0.10625 | 0.10486 | 0.10347 | 0.10208 | 0.10069 | 0.099306 | 0.097917 | 0.096528
| 14 | 0.097917 | 0.096528 | 0.095139 | 0.09375 | 0.092361 | 0.090972 | 0.089583 | 0.088194 | 0.086806
| 14.5 | 0.089583 | 0.088194 | 0.086806 | 0.085417 | 0.084028 | 0.082639 | 0.08125 | 0.079167 | 0.077778
| 15 | 0.081944 | 0.080556 | 0.079167 | 0.077778 | 0.076389 | 0.075 | 0.073611 | 0.072222 | 0.070833
| 15.5 | 0.075 | 0.073611 | 0.072222 | 0.070833 | 0.069444 | 0.098 | 0.096 | 0.094 | 0.092
| 16 | 0.098 | 0.097 | 0.095 | 0.093 | 0.091 | 0.089 | 0.087 | 0.086 | 0.084
| 16.5 | 0.09 | 0.088 | 0.087 | 0.085 | 0.083 | 0.082 | 0.08 | 0.079 | 0.077
| 17 | 0.083 | 0.082 | 0.08 | 0.078 | 0.077 | 0.075 | 0.074 | 0.073 | 0.071
| 17.5 | 0.077 | 0.076 | 0.074 | 0.073 | 0.071 | 0.07 | 0.069 | 0.068 | 0.066
| 18 | 0.072 | 0.071 | 0.069 | 0.068 | 0.067 | 0.065 | 0.064 | 0.063 | 0.062
| 18.5 | 0.068 | 0.066 | 0.065 | 0.064 | 0.063 | 0.062 | 0.06 | 0.059 | 0.058
| 19 | 0.064 | 0.063 | 0.062 | 0.06 | 0.059 | 0.058 | 0.057 | 0.056 | 0.055
| 19.5 | 0.061 | 0.06 | 0.059 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053 | 0.053
| 20 | 0.058 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053 | 0.052 | 0.051 | 0.05
| 20.5 | 0.053 | 0.052 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046
| 21 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.045 | 0.044 | 0.043 | 0.042
| 21.5 | 0.044 | 0.043 | 0.043 | 0.042 | 0.041 | 0.04 | 0.04 | 0.039 | 0.038
| 22 | 0.04 | 0.04 | 0.039 | 0.038 | 0.038 | 0.037 | 0.036 | 0.036 | 0.035
| 22.5 | 0.037 | 0.036 | 0.036 | 0.035 | 0.034 | 0.034 | 0.033 | 0.033 | 0.032
| 23 | 0.034 | 0.033 | 0.033 | 0.032 | 0.032 | 0.031 | 0.03 | 0.03 | 0.029
| 23.5 | 0.031 | 0.03 | 0.03 | 0.029 | 0.029 | 0.028 | 0.028 | 0.027 | 0.027
| 24 | 0.028 | 0.028 | 0.027 | 0.027 | 0.026 | 0.026 | 0.025 | 0.025 | 0.025
| 24.5 | 0.026 | 0.026 | 0.025 | 0.025 | 0.024 | 0.024 | 0.023 | 0.023 | 0.023
| 25 | 0.024 | 0.024 | 0.023 | 0.023 | 0.023 | 0.022 | 0.022 | 0.021 | 0.021
| 25.5 | 0.022 | 0.022 | 0.022 | 0.021 | 0.021 | 0.02 | 0.02 | 0.02 | 0.019
| 26 | 0.021 | 0.02 | 0.02 | 0.02 | 0.019 | 0.019 | 0.019 | 0.018 | 0.018