## Sheet1
PROPERTIES
General
Name | Nordex N163/5.X Class B 108m 2,8MW
Manufacturer | Nordex
Hub Height | 108
Power
Rated Power | 2800
Peak Power | 2800
Power Regulation Type | Pitch
Voltage | 750
Rotor
Rotor diameter | 163
Number of blades | 3
Rated RPM | 11.8
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 26
Restart Wind Speed | 25.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 45
High Temperature Restart | 40
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | B
Values
Certification | IEC 3rd Edition
Vave | 6.5-8
Vref | 38.8-40.3
Design TI | 0.16

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 30 | 33 | 35 | 37 | 39 | 42 | 44 | 46 | 48
| 3.5 | 126 | 130 | 134 | 139 | 143 | 148 | 152 | 156 | 161
| 4 | 253 | 260 | 267 | 275 | 282 | 289 | 296 | 304 | 311
| 4.5 | 410 | 421 | 432 | 442 | 453 | 464 | 475 | 486 | 497
| 5 | 598 | 613 | 628 | 643 | 658 | 673 | 688 | 703 | 718
| 5.5 | 811 | 831 | 851 | 870 | 890 | 910 | 930 | 950 | 970
| 6 | 1026 | 1050 | 1075 | 1100 | 1125 | 1150 | 1174 | 1199 | 1224
| 6.5 | 1227 | 1257 | 1286 | 1315 | 1345 | 1374 | 1403 | 1433 | 1462
| 7 | 1412 | 1446 | 1479 | 1513 | 1546 | 1580 | 1613 | 1647 | 1680
| 7.5 | 1583 | 1621 | 1658 | 1695 | 1733 | 1770 | 1807 | 1845 | 1882
| 8 | 1744 | 1785 | 1826 | 1867 | 1908 | 1949 | 1990 | 2031 | 2072
| 8.5 | 1900 | 1945 | 1989 | 2034 | 2078 | 2123 | 2167 | 2212 | 2256
| 9 | 2055 | 2103 | 2151 | 2199 | 2247 | 2295 | 2343 | 2390 | 2436
| 9.5 | 2201 | 2252 | 2304 | 2356 | 2405 | 2455 | 2498 | 2537 | 2575
| 10 | 2342 | 2397 | 2449 | 2500 | 2542 | 2582 | 2617 | 2647 | 2676
| 10.5 | 2476 | 2529 | 2571 | 2612 | 2645 | 2677 | 2703 | 2724 | 2745
| 11 | 2586 | 2628 | 2662 | 2695 | 2719 | 2742 | 2760 | 2773 | 2786
| 11.5 | 2667 | 2701 | 2725 | 2750 | 2766 | 2781 | 2790 | 2796 | 2800
| 12 | 2725 | 2750 | 2766 | 2782 | 2790 | 2797 | 2800 | 2800 | 2800
| 12.5 | 2765 | 2782 | 2790 | 2798 | 2800 | 2800 | 2800 | 2800 | 2800
| 13 | 2789 | 2798 | 2799 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800
| 13.5 | 2799 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800
| 14 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800
| 14.5 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800
| 15 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800
| 15.5 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800
| 16 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800
| 16.5 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800
| 17 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800
| 17.5 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800
| 18 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800
| 18.5 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800
| 19 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800
| 19.5 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800
| 20 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800
| 20.5 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800
| 21 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800
| 21.5 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800
| 22 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800
| 22.5 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800
| 23 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800
| 23.5 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800
| 24 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800
| 24.5 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800
| 25 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800
| 25.5 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800
| 26 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764
| 3.5 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208
| 4 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819
| 4.5 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639
| 5 | 0.55486 | 0.55486 | 0.55486 | 0.55486 | 0.55486 | 0.55486 | 0.55486 | 0.55486 | 0.55486
| 5.5 | 0.51944 | 0.51944 | 0.51944 | 0.51944 | 0.51944 | 0.51944 | 0.51944 | 0.51944 | 0.51944
| 6 | 0.47708 | 0.47708 | 0.47708 | 0.47708 | 0.47708 | 0.47708 | 0.47708 | 0.47708 | 0.47708
| 6.5 | 0.43264 | 0.43264 | 0.43264 | 0.43264 | 0.43264 | 0.43264 | 0.43264 | 0.43264 | 0.43264
| 7 | 0.38819 | 0.38819 | 0.38819 | 0.38819 | 0.38819 | 0.38819 | 0.38819 | 0.38819 | 0.38819
| 7.5 | 0.34375 | 0.34375 | 0.34375 | 0.34375 | 0.34375 | 0.34375 | 0.34375 | 0.34375 | 0.34375
| 8 | 0.30417 | 0.30417 | 0.30417 | 0.30417 | 0.30417 | 0.30417 | 0.30417 | 0.30417 | 0.30417
| 8.5 | 0.27014 | 0.27014 | 0.27014 | 0.27014 | 0.27014 | 0.27014 | 0.26944 | 0.26944 | 0.26875
| 9 | 0.24097 | 0.24097 | 0.24097 | 0.24097 | 0.24028 | 0.24028 | 0.23958 | 0.23889 | 0.23819
| 9.5 | 0.21667 | 0.21597 | 0.21597 | 0.21528 | 0.21458 | 0.21389 | 0.21319 | 0.21181 | 0.21111
| 10 | 0.19444 | 0.19444 | 0.19375 | 0.19306 | 0.19167 | 0.19097 | 0.18958 | 0.18889 | 0.1875
| 10.5 | 0.175 | 0.17431 | 0.17361 | 0.17292 | 0.17153 | 0.17083 | 0.16944 | 0.16806 | 0.16667
| 11 | 0.15833 | 0.15694 | 0.15625 | 0.15486 | 0.15417 | 0.15278 | 0.15139 | 0.15 | 0.14861
| 11.5 | 0.14306 | 0.14167 | 0.14028 | 0.13958 | 0.13819 | 0.13681 | 0.13542 | 0.13403 | 0.13264
| 12 | 0.12917 | 0.12778 | 0.12708 | 0.12569 | 0.12431 | 0.12292 | 0.12153 | 0.12014 | 0.11875
| 12.5 | 0.11736 | 0.11597 | 0.11458 | 0.11319 | 0.11181 | 0.11042 | 0.10903 | 0.10764 | 0.10625
| 13 | 0.10625 | 0.10486 | 0.10347 | 0.10208 | 0.10069 | 0.099306 | 0.097917 | 0.096528 | 0.094444
| 13.5 | 0.096528 | 0.095139 | 0.09375 | 0.092361 | 0.090972 | 0.089583 | 0.088194 | 0.086111 | 0.084722
| 14 | 0.0875 | 0.086111 | 0.084722 | 0.083333 | 0.081944 | 0.080556 | 0.079167 | 0.077778 | 0.075694
| 14.5 | 0.079861 | 0.078472 | 0.077083 | 0.075694 | 0.074306 | 0.072222 | 0.070833 | 0.070139 | 0.099
| 15 | 0.072222 | 0.070833 | 0.069444 | 0.098 | 0.096 | 0.095 | 0.093 | 0.091 | 0.089
| 15.5 | 0.095 | 0.093 | 0.091 | 0.089 | 0.088 | 0.086 | 0.084 | 0.083 | 0.081
| 16 | 0.087 | 0.085 | 0.083 | 0.082 | 0.08 | 0.078 | 0.077 | 0.076 | 0.074
| 16.5 | 0.08 | 0.078 | 0.076 | 0.075 | 0.073 | 0.072 | 0.071 | 0.069 | 0.068
| 17 | 0.073 | 0.072 | 0.071 | 0.069 | 0.068 | 0.067 | 0.065 | 0.064 | 0.063
| 17.5 | 0.068 | 0.067 | 0.066 | 0.064 | 0.063 | 0.062 | 0.061 | 0.06 | 0.059
| 18 | 0.064 | 0.063 | 0.061 | 0.06 | 0.059 | 0.058 | 0.057 | 0.056 | 0.055
| 18.5 | 0.06 | 0.059 | 0.058 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053 | 0.052
| 19 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049
| 19.5 | 0.054 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.047
| 20 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.045
| 20.5 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.041
| 21 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.04 | 0.039 | 0.038 | 0.038
| 21.5 | 0.04 | 0.039 | 0.038 | 0.037 | 0.037 | 0.036 | 0.035 | 0.034 | 0.034
| 22 | 0.036 | 0.036 | 0.035 | 0.034 | 0.033 | 0.033 | 0.032 | 0.031 | 0.031
| 22.5 | 0.033 | 0.033 | 0.032 | 0.031 | 0.031 | 0.03 | 0.029 | 0.029 | 0.029
| 23 | 0.03 | 0.03 | 0.029 | 0.029 | 0.028 | 0.028 | 0.027 | 0.026 | 0.026
| 23.5 | 0.028 | 0.027 | 0.027 | 0.026 | 0.025 | 0.025 | 0.024 | 0.024 | 0.024
| 24 | 0.025 | 0.025 | 0.025 | 0.024 | 0.024 | 0.023 | 0.023 | 0.022 | 0.022
| 24.5 | 0.023 | 0.023 | 0.023 | 0.022 | 0.022 | 0.021 | 0.021 | 0.02 | 0.02
| 25 | 0.022 | 0.021 | 0.021 | 0.02 | 0.02 | 0.02 | 0.019 | 0.019 | 0.019
| 25.5 | 0.02 | 0.02 | 0.019 | 0.019 | 0.018 | 0.018 | 0.018 | 0.017 | 0.017
| 26 | 0.019 | 0.018 | 0.018 | 0.018 | 0.017 | 0.017 | 0.016 | 0.016 | 0.016