## Sheet1
PROPERTIES
General
Name | Nordex N163/5.X Class B 2,58MW
Manufacturer | Nordex
Hub Height | 118 | 148 | 159 | 164
Power
Rated Power | 2580
Peak Power | 2580
Power Regulation Type | Pitch
Voltage | 750
Rotor
Rotor diameter | 163
Number of blades | 3
Rated RPM | 11.8
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 26
Restart Wind Speed | 25.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 45
High Temperature Restart | 40
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | B
Values
Certification | IEC 3rd Edition
Vave | 6.5-8
Vref | 38.8-40.3
Design TI | 0.16

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 36 | 39 | 41 | 43 | 45 | 48 | 50 | 52 | 54
| 3.5 | 133 | 137 | 142 | 146 | 150 | 155 | 159 | 164 | 168
| 4 | 261 | 268 | 276 | 283 | 290 | 298 | 305 | 313 | 320
| 4.5 | 419 | 430 | 441 | 452 | 463 | 474 | 485 | 496 | 507
| 5 | 609 | 624 | 639 | 655 | 670 | 685 | 700 | 715 | 731
| 5.5 | 816 | 836 | 856 | 876 | 896 | 916 | 936 | 956 | 975
| 6 | 1020 | 1044 | 1069 | 1093 | 1118 | 1142 | 1166 | 1191 | 1215
| 6.5 | 1207 | 1236 | 1264 | 1293 | 1322 | 1350 | 1379 | 1408 | 1436
| 7 | 1378 | 1411 | 1444 | 1476 | 1509 | 1541 | 1574 | 1606 | 1639
| 7.5 | 1537 | 1574 | 1610 | 1646 | 1682 | 1718 | 1754 | 1790 | 1826
| 8 | 1689 | 1728 | 1768 | 1807 | 1847 | 1886 | 1926 | 1965 | 2004
| 8.5 | 1837 | 1880 | 1923 | 1966 | 2009 | 2051 | 2094 | 2137 | 2180
| 9 | 1982 | 2028 | 2074 | 2120 | 2166 | 2211 | 2256 | 2292 | 2328
| 9.5 | 2118 | 2168 | 2216 | 2264 | 2307 | 2344 | 2381 | 2408 | 2436
| 10 | 2249 | 2299 | 2341 | 2380 | 2415 | 2443 | 2472 | 2491 | 2510
| 10.5 | 2362 | 2402 | 2436 | 2466 | 2492 | 2513 | 2533 | 2545 | 2557
| 11 | 2445 | 2477 | 2502 | 2524 | 2543 | 2556 | 2569 | 2573 | 2577
| 11.5 | 2505 | 2528 | 2545 | 2560 | 2570 | 2576 | 2580 | 2580 | 2580
| 12 | 2545 | 2560 | 2570 | 2576 | 2580 | 2580 | 2580 | 2580 | 2580
| 12.5 | 2569 | 2577 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 13 | 2579 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 13.5 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 14 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 14.5 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 15 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 15.5 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 16 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 16.5 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 17 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 17.5 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 18 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 18.5 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 19 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 19.5 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 20 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 20.5 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 21 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 21.5 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 22 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 22.5 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 23 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 23.5 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 24 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 24.5 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 25 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 25.5 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 26 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764
| 3.5 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208
| 4 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819
| 4.5 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639
| 5 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55
| 5.5 | 0.51042 | 0.51042 | 0.51042 | 0.51042 | 0.51042 | 0.51042 | 0.51042 | 0.51042 | 0.51042
| 6 | 0.46528 | 0.46528 | 0.46528 | 0.46528 | 0.46528 | 0.46528 | 0.46528 | 0.46528 | 0.46528
| 6.5 | 0.41944 | 0.41944 | 0.41944 | 0.41944 | 0.41944 | 0.41944 | 0.41944 | 0.41944 | 0.41944
| 7 | 0.37361 | 0.37361 | 0.37361 | 0.37361 | 0.37361 | 0.37361 | 0.37361 | 0.37361 | 0.37361
| 7.5 | 0.32847 | 0.32847 | 0.32847 | 0.32847 | 0.32847 | 0.32847 | 0.32847 | 0.32847 | 0.32847
| 8 | 0.28889 | 0.28889 | 0.28889 | 0.28889 | 0.28889 | 0.28889 | 0.28889 | 0.28889 | 0.28819
| 8.5 | 0.25625 | 0.25625 | 0.25625 | 0.25625 | 0.25625 | 0.25625 | 0.25556 | 0.25486 | 0.25417
| 9 | 0.22917 | 0.22917 | 0.22847 | 0.22847 | 0.22778 | 0.22708 | 0.22639 | 0.225 | 0.22431
| 9.5 | 0.20486 | 0.20486 | 0.20417 | 0.20347 | 0.20278 | 0.20139 | 0.20069 | 0.19931 | 0.19792
| 10 | 0.18403 | 0.18333 | 0.18264 | 0.18125 | 0.18056 | 0.17917 | 0.17847 | 0.17639 | 0.17569
| 10.5 | 0.16528 | 0.16389 | 0.16319 | 0.16181 | 0.16111 | 0.15972 | 0.15833 | 0.15694 | 0.15556
| 11 | 0.14861 | 0.14722 | 0.14653 | 0.14514 | 0.14375 | 0.14236 | 0.14097 | 0.13958 | 0.13819
| 11.5 | 0.13403 | 0.13264 | 0.13125 | 0.12986 | 0.12917 | 0.12708 | 0.12569 | 0.12431 | 0.12292
| 12 | 0.12083 | 0.11944 | 0.11806 | 0.11667 | 0.11528 | 0.11389 | 0.1125 | 0.11111 | 0.10903
| 12.5 | 0.10903 | 0.10764 | 0.10625 | 0.10486 | 0.10347 | 0.10208 | 0.10069 | 0.099306 | 0.097222
| 13 | 0.098611 | 0.097222 | 0.095833 | 0.094444 | 0.093056 | 0.091667 | 0.090278 | 0.088194 | 0.086806
| 13.5 | 0.089583 | 0.088194 | 0.086806 | 0.085417 | 0.083333 | 0.081944 | 0.080556 | 0.079167 | 0.077778
| 14 | 0.08125 | 0.079861 | 0.078472 | 0.076389 | 0.075 | 0.073611 | 0.072222 | 0.070833 | 0.069444
| 14.5 | 0.073611 | 0.072222 | 0.070833 | 0.069444 | 0.098 | 0.096 | 0.094 | 0.092 | 0.091
| 15 | 0.096 | 0.094 | 0.092 | 0.09 | 0.088 | 0.087 | 0.085 | 0.084 | 0.082
| 15.5 | 0.087 | 0.086 | 0.084 | 0.082 | 0.08 | 0.079 | 0.077 | 0.076 | 0.075
| 16 | 0.08 | 0.078 | 0.076 | 0.075 | 0.074 | 0.072 | 0.071 | 0.07 | 0.068
| 16.5 | 0.073 | 0.072 | 0.07 | 0.069 | 0.068 | 0.066 | 0.065 | 0.064 | 0.063
| 17 | 0.068 | 0.066 | 0.065 | 0.064 | 0.062 | 0.061 | 0.06 | 0.059 | 0.058
| 17.5 | 0.063 | 0.062 | 0.06 | 0.059 | 0.058 | 0.057 | 0.056 | 0.055 | 0.054
| 18 | 0.059 | 0.058 | 0.056 | 0.055 | 0.054 | 0.053 | 0.052 | 0.052 | 0.051
| 18.5 | 0.055 | 0.054 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.049 | 0.048
| 19 | 0.052 | 0.051 | 0.05 | 0.049 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045
| 19.5 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.045 | 0.044 | 0.043
| 20 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.043 | 0.042 | 0.041
| 20.5 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.04 | 0.04 | 0.039 | 0.038
| 21 | 0.04 | 0.04 | 0.039 | 0.038 | 0.037 | 0.036 | 0.036 | 0.035 | 0.034
| 21.5 | 0.037 | 0.036 | 0.035 | 0.034 | 0.034 | 0.033 | 0.033 | 0.032 | 0.031
| 22 | 0.033 | 0.033 | 0.032 | 0.031 | 0.031 | 0.03 | 0.03 | 0.029 | 0.029
| 22.5 | 0.031 | 0.03 | 0.029 | 0.029 | 0.028 | 0.027 | 0.027 | 0.027 | 0.026
| 23 | 0.028 | 0.028 | 0.027 | 0.026 | 0.026 | 0.025 | 0.025 | 0.025 | 0.024
| 23.5 | 0.025 | 0.025 | 0.024 | 0.024 | 0.023 | 0.023 | 0.023 | 0.022 | 0.022
| 24 | 0.024 | 0.023 | 0.023 | 0.022 | 0.022 | 0.021 | 0.021 | 0.021 | 0.02
| 24.5 | 0.022 | 0.021 | 0.021 | 0.02 | 0.02 | 0.019 | 0.019 | 0.019 | 0.018
| 25 | 0.02 | 0.02 | 0.019 | 0.019 | 0.018 | 0.018 | 0.018 | 0.018 | 0.017
| 25.5 | 0.018 | 0.018 | 0.018 | 0.017 | 0.017 | 0.017 | 0.017 | 0.016 | 0.016
| 26 | 0.017 | 0.017 | 0.016 | 0.016 | 0.016 | 0.015 | 0.015 | 0.015 | 0.015