## Sheet1
PROPERTIES
General
Name | Nordex N163/5.X Class B 108m 2,58MW
Manufacturer | Nordex
Hub Height | 108
Power
Rated Power | 2580
Peak Power | 2580
Power Regulation Type | Pitch
Voltage | 750
Rotor
Rotor diameter | 163
Number of blades | 3
Rated RPM | 11.8
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 26
Restart Wind Speed | 25.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 45
High Temperature Restart | 40
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | B
Values
Certification | IEC 3rd Edition
Vave | 6.5-8
Vref | 38.8-40.3
Design TI | 0.16

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 30 | 32 | 35 | 37 | 39 | 41 | 44 | 46 | 48
| 3.5 | 126 | 130 | 134 | 139 | 143 | 148 | 152 | 156 | 161
| 4 | 253 | 260 | 267 | 275 | 282 | 289 | 296 | 304 | 311
| 4.5 | 410 | 421 | 431 | 442 | 453 | 464 | 475 | 486 | 497
| 5 | 598 | 613 | 628 | 643 | 658 | 673 | 688 | 703 | 718
| 5.5 | 803 | 823 | 843 | 862 | 882 | 902 | 922 | 942 | 961
| 6 | 1005 | 1029 | 1054 | 1078 | 1102 | 1127 | 1151 | 1175 | 1200
| 6.5 | 1191 | 1220 | 1248 | 1277 | 1305 | 1334 | 1362 | 1391 | 1419
| 7 | 1362 | 1394 | 1426 | 1459 | 1491 | 1523 | 1556 | 1588 | 1620
| 7.5 | 1520 | 1555 | 1591 | 1627 | 1663 | 1699 | 1735 | 1771 | 1807
| 8 | 1670 | 1709 | 1749 | 1788 | 1827 | 1867 | 1906 | 1945 | 1984
| 8.5 | 1818 | 1860 | 1903 | 1946 | 1988 | 2031 | 2074 | 2116 | 2159
| 9 | 1961 | 2007 | 2053 | 2099 | 2145 | 2190 | 2236 | 2275 | 2310
| 9.5 | 2098 | 2147 | 2196 | 2243 | 2290 | 2328 | 2365 | 2396 | 2423
| 10 | 2229 | 2279 | 2325 | 2363 | 2402 | 2431 | 2459 | 2482 | 2501
| 10.5 | 2346 | 2386 | 2423 | 2453 | 2483 | 2504 | 2525 | 2540 | 2552
| 11 | 2433 | 2464 | 2493 | 2515 | 2537 | 2550 | 2563 | 2571 | 2575
| 11.5 | 2496 | 2519 | 2540 | 2554 | 2568 | 2573 | 2579 | 2580 | 2580
| 12 | 2539 | 2554 | 2567 | 2574 | 2580 | 2580 | 2580 | 2580 | 2580
| 12.5 | 2566 | 2574 | 2579 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 13 | 2579 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 13.5 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 14 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 14.5 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 15 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 15.5 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 16 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 16.5 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 17 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 17.5 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 18 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 18.5 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 19 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 19.5 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 20 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 20.5 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 21 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 21.5 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 22 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 22.5 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 23 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 23.5 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 24 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 24.5 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 25 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 25.5 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580
| 26 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580 | 2580

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764
| 3.5 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208
| 4 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819
| 4.5 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639
| 5 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55
| 5.5 | 0.51042 | 0.51042 | 0.51042 | 0.51042 | 0.51042 | 0.51042 | 0.51042 | 0.51042 | 0.51042
| 6 | 0.46528 | 0.46528 | 0.46528 | 0.46528 | 0.46528 | 0.46528 | 0.46528 | 0.46528 | 0.46528
| 6.5 | 0.41944 | 0.41944 | 0.41944 | 0.41944 | 0.41944 | 0.41944 | 0.41944 | 0.41944 | 0.41944
| 7 | 0.37361 | 0.37361 | 0.37361 | 0.37361 | 0.37361 | 0.37361 | 0.37361 | 0.37361 | 0.37361
| 7.5 | 0.32847 | 0.32847 | 0.32847 | 0.32847 | 0.32847 | 0.32847 | 0.32847 | 0.32847 | 0.32847
| 8 | 0.28889 | 0.28889 | 0.28889 | 0.28889 | 0.28889 | 0.28889 | 0.28889 | 0.28889 | 0.28819
| 8.5 | 0.25625 | 0.25625 | 0.25625 | 0.25625 | 0.25625 | 0.25625 | 0.25556 | 0.25486 | 0.25417
| 9 | 0.22917 | 0.22917 | 0.22847 | 0.22847 | 0.22778 | 0.22708 | 0.22639 | 0.22569 | 0.22431
| 9.5 | 0.20486 | 0.20486 | 0.20417 | 0.20347 | 0.20278 | 0.20208 | 0.20069 | 0.2 | 0.19861
| 10 | 0.18403 | 0.18333 | 0.18264 | 0.18194 | 0.18056 | 0.17986 | 0.17847 | 0.17708 | 0.17569
| 10.5 | 0.16528 | 0.16458 | 0.16389 | 0.1625 | 0.16181 | 0.16042 | 0.15903 | 0.15764 | 0.15625
| 11 | 0.14861 | 0.14792 | 0.14653 | 0.14583 | 0.14444 | 0.14306 | 0.14167 | 0.14028 | 0.13889
| 11.5 | 0.13403 | 0.13333 | 0.13194 | 0.13056 | 0.12917 | 0.12778 | 0.12639 | 0.125 | 0.12361
| 12 | 0.12153 | 0.12014 | 0.11875 | 0.11736 | 0.11597 | 0.11458 | 0.11319 | 0.11181 | 0.10972
| 12.5 | 0.10972 | 0.10833 | 0.10694 | 0.10556 | 0.10417 | 0.10278 | 0.10139 | 0.1 | 0.097917
| 13 | 0.099306 | 0.097917 | 0.096528 | 0.095139 | 0.09375 | 0.092361 | 0.090972 | 0.088889 | 0.0875
| 13.5 | 0.089583 | 0.088194 | 0.086806 | 0.085417 | 0.084028 | 0.082639 | 0.08125 | 0.079861 | 0.078472
| 14 | 0.08125 | 0.079861 | 0.078472 | 0.077083 | 0.075694 | 0.074306 | 0.072917 | 0.071528 | 0.070139
| 14.5 | 0.074306 | 0.072917 | 0.071528 | 0.069444 | 0.098 | 0.097 | 0.095 | 0.093 | 0.091
| 15 | 0.097 | 0.095 | 0.093 | 0.091 | 0.089 | 0.087 | 0.086 | 0.084 | 0.083
| 15.5 | 0.088 | 0.086 | 0.084 | 0.083 | 0.081 | 0.08 | 0.078 | 0.077 | 0.075
| 16 | 0.08 | 0.079 | 0.077 | 0.076 | 0.074 | 0.073 | 0.071 | 0.07 | 0.069
| 16.5 | 0.074 | 0.072 | 0.071 | 0.069 | 0.068 | 0.067 | 0.066 | 0.064 | 0.063
| 17 | 0.068 | 0.067 | 0.065 | 0.064 | 0.063 | 0.062 | 0.061 | 0.06 | 0.059
| 17.5 | 0.063 | 0.062 | 0.061 | 0.06 | 0.059 | 0.057 | 0.056 | 0.055 | 0.055
| 18 | 0.059 | 0.058 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053 | 0.052 | 0.051
| 18.5 | 0.056 | 0.055 | 0.054 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048
| 19 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.046
| 19.5 | 0.05 | 0.049 | 0.048 | 0.047 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043
| 20 | 0.048 | 0.047 | 0.046 | 0.045 | 0.045 | 0.044 | 0.043 | 0.042 | 0.042
| 20.5 | 0.044 | 0.043 | 0.042 | 0.041 | 0.041 | 0.04 | 0.04 | 0.039 | 0.039
| 21 | 0.04 | 0.04 | 0.039 | 0.038 | 0.038 | 0.037 | 0.036 | 0.035 | 0.035
| 21.5 | 0.037 | 0.036 | 0.035 | 0.034 | 0.034 | 0.034 | 0.033 | 0.032 | 0.032
| 22 | 0.033 | 0.033 | 0.032 | 0.031 | 0.031 | 0.031 | 0.03 | 0.029 | 0.029
| 22.5 | 0.031 | 0.03 | 0.029 | 0.029 | 0.029 | 0.028 | 0.027 | 0.027 | 0.027
| 23 | 0.028 | 0.028 | 0.027 | 0.026 | 0.026 | 0.026 | 0.025 | 0.025 | 0.025
| 23.5 | 0.025 | 0.025 | 0.024 | 0.024 | 0.024 | 0.023 | 0.023 | 0.022 | 0.022
| 24 | 0.024 | 0.023 | 0.023 | 0.022 | 0.022 | 0.022 | 0.021 | 0.021 | 0.021
| 24.5 | 0.022 | 0.021 | 0.021 | 0.02 | 0.02 | 0.02 | 0.019 | 0.019 | 0.019
| 25 | 0.02 | 0.02 | 0.019 | 0.019 | 0.019 | 0.018 | 0.018 | 0.018 | 0.018
| 25.5 | 0.018 | 0.018 | 0.018 | 0.017 | 0.017 | 0.017 | 0.017 | 0.016 | 0.016
| 26 | 0.017 | 0.017 | 0.016 | 0.016 | 0.016 | 0.016 | 0.015 | 0.015 | 0.015