## Sheet1
PROPERTIES
General
Name | Nordex N163/5.X Class B 5,5MW
Manufacturer | Nordex
Hub Height | 118 | 120 | 148 | 159 | 164
Power
Rated Power | 5500
Peak Power | 5500
Power Regulation Type | Pitch
Voltage | 750
Rotor
Rotor diameter | 163
Number of blades | 3
Rated RPM | 11.8
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 26
Restart Wind Speed | 25.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 45
High Temperature Restart | 40
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | B
Values
Certification | IEC 3rd Edition
Vave | 6.5-8
Vref | 38.8-40.3
Design TI | 0.16

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 18 | 21 | 23 | 25 | 28 | 30 | 32 | 34 | 37 | 39 | 41 | 44 | 46 | 48 | 50 | 53 | 55
| 3.5 | 97 | 101 | 106 | 110 | 115 | 119 | 124 | 128 | 133 | 137 | 142 | 146 | 151 | 155 | 159 | 164 | 168
| 4 | 202 | 209 | 217 | 224 | 231 | 239 | 246 | 254 | 261 | 268 | 276 | 283 | 290 | 298 | 305 | 312 | 320
| 4.5 | 332 | 343 | 354 | 365 | 376 | 387 | 398 | 409 | 420 | 431 | 441 | 452 | 463 | 474 | 485 | 496 | 507
| 5 | 487 | 502 | 517 | 533 | 548 | 563 | 578 | 594 | 609 | 624 | 639 | 655 | 670 | 685 | 700 | 716 | 731
| 5.5 | 671 | 692 | 712 | 732 | 753 | 773 | 793 | 814 | 834 | 854 | 875 | 895 | 915 | 936 | 956 | 976 | 997
| 6 | 890 | 916 | 943 | 969 | 996 | 1022 | 1048 | 1075 | 1101 | 1127 | 1154 | 1180 | 1206 | 1232 | 1259 | 1285 | 1311
| 6.5 | 1148 | 1181 | 1214 | 1248 | 1281 | 1315 | 1348 | 1382 | 1415 | 1448 | 1482 | 1515 | 1549 | 1582 | 1615 | 1649 | 1682
| 7 | 1447 | 1489 | 1530 | 1572 | 1614 | 1655 | 1697 | 1739 | 1780 | 1822 | 1863 | 1905 | 1946 | 1988 | 2029 | 2071 | 2112
| 7.5 | 1792 | 1843 | 1895 | 1946 | 1997 | 2048 | 2099 | 2150 | 2201 | 2252 | 2303 | 2353 | 2404 | 2455 | 2506 | 2556 | 2605
| 8 | 2175 | 2236 | 2298 | 2359 | 2421 | 2482 | 2543 | 2605 | 2666 | 2727 | 2789 | 2850 | 2911 | 2972 | 3028 | 3081 | 3133
| 8.5 | 2569 | 2642 | 2714 | 2786 | 2858 | 2930 | 3002 | 3074 | 3146 | 3218 | 3290 | 3362 | 3433 | 3504 | 3559 | 3611 | 3661
| 9 | 2959 | 3042 | 3125 | 3207 | 3290 | 3373 | 3455 | 3538 | 3620 | 3702 | 3784 | 3867 | 3949 | 4026 | 4078 | 4126 | 4170
| 9.5 | 3332 | 3425 | 3517 | 3610 | 3703 | 3795 | 3888 | 3980 | 4073 | 4166 | 4258 | 4347 | 4436 | 4514 | 4560 | 4600 | 4633
| 10 | 3681 | 3784 | 3886 | 3988 | 4090 | 4192 | 4295 | 4396 | 4492 | 4589 | 4679 | 4753 | 4826 | 4890 | 4923 | 4951 | 4973
| 10.5 | 4011 | 4122 | 4233 | 4345 | 4457 | 4561 | 4663 | 4760 | 4839 | 4918 | 4991 | 5050 | 5109 | 5158 | 5180 | 5199 | 5214
| 11 | 4323 | 4444 | 4564 | 4673 | 4781 | 4868 | 4952 | 5031 | 5094 | 5157 | 5215 | 5259 | 5302 | 5336 | 5351 | 5364 | 5372
| 11.5 | 4622 | 4738 | 4851 | 4941 | 5030 | 5100 | 5167 | 5229 | 5277 | 5324 | 5366 | 5395 | 5423 | 5445 | 5454 | 5461 | 5464
| 12 | 4881 | 4979 | 5072 | 5145 | 5216 | 5270 | 5321 | 5367 | 5399 | 5430 | 5458 | 5471 | 5484 | 5494 | 5498 | 5500 | 5500
| 12.5 | 5084 | 5164 | 5240 | 5296 | 5351 | 5388 | 5423 | 5454 | 5470 | 5486 | 5498 | 5499 | 5500 | 5500 | 5500 | 5500 | 5500
| 13 | 5241 | 5303 | 5361 | 5401 | 5440 | 5461 | 5481 | 5496 | 5498 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 13.5 | 5355 | 5401 | 5442 | 5466 | 5489 | 5495 | 5499 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 14 | 5433 | 5462 | 5488 | 5495 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 14.5 | 5480 | 5493 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 15 | 5499 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 15.5 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 16 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 16.5 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 17 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 17.5 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 18 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 18.5 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 19 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 19.5 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 20 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 20.5 | 5493 | 5493 | 5493 | 5493 | 5493 | 5493 | 5493 | 5493 | 5493 | 5493 | 5493 | 5493 | 5493 | 5493 | 5493 | 5493 | 5493
| 21 | 5427 | 5427 | 5427 | 5427 | 5427 | 5427 | 5427 | 5427 | 5427 | 5427 | 5427 | 5427 | 5427 | 5427 | 5427 | 5427 | 5427
| 21.5 | 5307 | 5307 | 5307 | 5307 | 5307 | 5307 | 5307 | 5307 | 5307 | 5307 | 5307 | 5307 | 5307 | 5307 | 5307 | 5307 | 5307
| 22 | 5153 | 5153 | 5153 | 5153 | 5153 | 5153 | 5153 | 5153 | 5153 | 5153 | 5153 | 5153 | 5153 | 5153 | 5153 | 5153 | 5153
| 22.5 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005
| 23 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856
| 23.5 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708
| 24 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560
| 24.5 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418
| 25 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269
| 25.5 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121
| 26 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764
| 3.5 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208
| 4 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819
| 4.5 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639
| 5 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875
| 5.5 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458
| 6 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181
| 6.5 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042
| 7 | 0.55833 | 0.55833 | 0.55833 | 0.55833 | 0.55833 | 0.55833 | 0.55833 | 0.55833 | 0.55833 | 0.55833 | 0.55833 | 0.55833 | 0.55833 | 0.55833 | 0.55764 | 0.55556 | 0.55417
| 7.5 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54375 | 0.54097 | 0.53819
| 8 | 0.52708 | 0.52708 | 0.52708 | 0.52708 | 0.52708 | 0.52708 | 0.52708 | 0.52708 | 0.52708 | 0.52708 | 0.52708 | 0.52708 | 0.52708 | 0.52639 | 0.52292 | 0.51875 | 0.51528
| 8.5 | 0.50278 | 0.50278 | 0.50278 | 0.50278 | 0.50278 | 0.50278 | 0.50278 | 0.50278 | 0.50278 | 0.50278 | 0.50278 | 0.50278 | 0.50278 | 0.50208 | 0.49792 | 0.49236 | 0.4875
| 9 | 0.47569 | 0.47569 | 0.47569 | 0.47569 | 0.47569 | 0.47569 | 0.47569 | 0.47569 | 0.47569 | 0.47569 | 0.475 | 0.47431 | 0.47292 | 0.47153 | 0.46597 | 0.46042 | 0.45486
| 9.5 | 0.44722 | 0.44722 | 0.44722 | 0.44722 | 0.44722 | 0.44722 | 0.44653 | 0.44653 | 0.44514 | 0.44375 | 0.44236 | 0.44097 | 0.43889 | 0.43681 | 0.43056 | 0.425 | 0.41875
| 10 | 0.41806 | 0.41806 | 0.41806 | 0.41736 | 0.41736 | 0.41597 | 0.41458 | 0.41319 | 0.41111 | 0.40972 | 0.40764 | 0.40556 | 0.40278 | 0.4 | 0.39444 | 0.38819 | 0.38194
| 10.5 | 0.38819 | 0.3875 | 0.3875 | 0.38611 | 0.38472 | 0.38264 | 0.38125 | 0.37917 | 0.37708 | 0.375 | 0.37222 | 0.36944 | 0.36667 | 0.36389 | 0.35764 | 0.35139 | 0.34514
| 11 | 0.35764 | 0.35625 | 0.35556 | 0.35347 | 0.35208 | 0.34931 | 0.34722 | 0.34514 | 0.34236 | 0.33958 | 0.3375 | 0.33403 | 0.33125 | 0.32778 | 0.32153 | 0.31528 | 0.30903
| 11.5 | 0.32639 | 0.325 | 0.32361 | 0.32083 | 0.31875 | 0.31667 | 0.31389 | 0.31111 | 0.30833 | 0.30556 | 0.30278 | 0.29931 | 0.29653 | 0.29306 | 0.28681 | 0.28125 | 0.27569
| 12 | 0.29722 | 0.29514 | 0.29306 | 0.29097 | 0.28819 | 0.28542 | 0.28264 | 0.27986 | 0.27708 | 0.27361 | 0.27083 | 0.26736 | 0.26458 | 0.26042 | 0.25556 | 0.25 | 0.24514
| 12.5 | 0.27083 | 0.26875 | 0.26597 | 0.26319 | 0.26111 | 0.25764 | 0.25486 | 0.25208 | 0.24861 | 0.24583 | 0.24236 | 0.23889 | 0.23611 | 0.23194 | 0.22778 | 0.22292 | 0.21806
| 13 | 0.24722 | 0.24444 | 0.24167 | 0.23889 | 0.23611 | 0.23333 | 0.22986 | 0.22708 | 0.22361 | 0.22083 | 0.21736 | 0.21389 | 0.21042 | 0.20694 | 0.20278 | 0.19861 | 0.19444
| 13.5 | 0.22569 | 0.22292 | 0.22014 | 0.21667 | 0.21389 | 0.21111 | 0.20764 | 0.20486 | 0.20139 | 0.19792 | 0.19514 | 0.19097 | 0.18819 | 0.18472 | 0.18056 | 0.17708 | 0.17361
| 14 | 0.20556 | 0.20278 | 0.2 | 0.19722 | 0.19444 | 0.19097 | 0.1875 | 0.18472 | 0.18125 | 0.17778 | 0.17431 | 0.17083 | 0.16736 | 0.16458 | 0.16111 | 0.15764 | 0.15417
| 14.5 | 0.18819 | 0.18542 | 0.18194 | 0.17917 | 0.17639 | 0.17292 | 0.16944 | 0.16667 | 0.16319 | 0.15972 | 0.15625 | 0.15278 | 0.14931 | 0.14653 | 0.14375 | 0.14028 | 0.1375
| 15 | 0.17222 | 0.16875 | 0.16597 | 0.16319 | 0.15972 | 0.15625 | 0.15347 | 0.15 | 0.14653 | 0.14306 | 0.14028 | 0.13681 | 0.13403 | 0.13125 | 0.12847 | 0.12639 | 0.12361
| 15.5 | 0.15764 | 0.15417 | 0.15139 | 0.14792 | 0.14514 | 0.14167 | 0.13819 | 0.13542 | 0.13194 | 0.12917 | 0.12639 | 0.12361 | 0.12083 | 0.11875 | 0.11597 | 0.11389 | 0.11181
| 16 | 0.14375 | 0.14097 | 0.13819 | 0.13472 | 0.13194 | 0.12847 | 0.125 | 0.12222 | 0.11944 | 0.11667 | 0.11458 | 0.11181 | 0.10972 | 0.10764 | 0.10556 | 0.10347 | 0.10139
| 16.5 | 0.13194 | 0.12917 | 0.12569 | 0.12292 | 0.11944 | 0.11667 | 0.11389 | 0.11111 | 0.10903 | 0.10625 | 0.10417 | 0.10208 | 0.1 | 0.097917 | 0.095833 | 0.094444 | 0.092361
| 17 | 0.12153 | 0.11875 | 0.11528 | 0.1125 | 0.10972 | 0.10694 | 0.10417 | 0.10208 | 0.1 | 0.097917 | 0.095833 | 0.09375 | 0.091667 | 0.090278 | 0.088194 | 0.086806 | 0.085417
| 17.5 | 0.1125 | 0.10903 | 0.10625 | 0.10347 | 0.10139 | 0.098611 | 0.096528 | 0.094444 | 0.092361 | 0.090278 | 0.088194 | 0.086806 | 0.084722 | 0.083333 | 0.081944 | 0.080556 | 0.079167
| 18 | 0.10417 | 0.10139 | 0.098611 | 0.096528 | 0.09375 | 0.091667 | 0.089583 | 0.0875 | 0.086111 | 0.084028 | 0.082639 | 0.080556 | 0.079167 | 0.077778 | 0.076389 | 0.075 | 0.073611
| 18.5 | 0.097222 | 0.095139 | 0.092361 | 0.090278 | 0.088194 | 0.086111 | 0.084028 | 0.081944 | 0.080556 | 0.078472 | 0.077083 | 0.075694 | 0.074306 | 0.072917 | 0.071528 | 0.070139 | 0.099
| 19 | 0.091667 | 0.089583 | 0.086806 | 0.084722 | 0.082639 | 0.08125 | 0.079167 | 0.077778 | 0.075694 | 0.074306 | 0.072917 | 0.071528 | 0.070139 | 0.099 | 0.097 | 0.095 | 0.094
| 19.5 | 0.086806 | 0.084722 | 0.082639 | 0.080556 | 0.078472 | 0.076389 | 0.075 | 0.073611 | 0.072222 | 0.070139 | 0.099 | 0.097 | 0.096 | 0.094 | 0.092 | 0.091 | 0.089
| 20 | 0.082639 | 0.080556 | 0.078472 | 0.076389 | 0.075 | 0.072917 | 0.071528 | 0.070139 | 0.099 | 0.097 | 0.095 | 0.093 | 0.091 | 0.09 | 0.088 | 0.086 | 0.085
| 20.5 | 0.075694 | 0.074306 | 0.072222 | 0.070139 | 0.099 | 0.097 | 0.095 | 0.093 | 0.091 | 0.089 | 0.087 | 0.086 | 0.084 | 0.083 | 0.081 | 0.079 | 0.078
| 21 | 0.069444 | 0.098 | 0.095 | 0.093 | 0.091 | 0.088 | 0.087 | 0.085 | 0.083 | 0.082 | 0.08 | 0.078 | 0.077 | 0.076 | 0.074 | 0.072 | 0.071
| 21.5 | 0.091 | 0.088 | 0.086 | 0.084 | 0.082 | 0.08 | 0.078 | 0.077 | 0.075 | 0.074 | 0.072 | 0.071 | 0.069 | 0.069 | 0.067 | 0.066 | 0.065
| 22 | 0.083 | 0.081 | 0.079 | 0.077 | 0.075 | 0.073 | 0.072 | 0.07 | 0.069 | 0.068 | 0.066 | 0.065 | 0.063 | 0.063 | 0.061 | 0.06 | 0.059
| 22.5 | 0.076 | 0.074 | 0.072 | 0.07 | 0.069 | 0.067 | 0.066 | 0.064 | 0.063 | 0.062 | 0.061 | 0.059 | 0.058 | 0.057 | 0.056 | 0.055 | 0.054
| 23 | 0.07 | 0.068 | 0.066 | 0.064 | 0.063 | 0.062 | 0.06 | 0.059 | 0.058 | 0.057 | 0.056 | 0.054 | 0.053 | 0.053 | 0.052 | 0.05 | 0.05
| 23.5 | 0.063 | 0.062 | 0.06 | 0.058 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053 | 0.052 | 0.05 | 0.049 | 0.048 | 0.048 | 0.047 | 0.046 | 0.045
| 24 | 0.058 | 0.057 | 0.055 | 0.054 | 0.053 | 0.051 | 0.05 | 0.049 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.042
| 24.5 | 0.054 | 0.052 | 0.051 | 0.05 | 0.049 | 0.047 | 0.046 | 0.045 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.041 | 0.04 | 0.039 | 0.038
| 25 | 0.05 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.04 | 0.039 | 0.038 | 0.038 | 0.037 | 0.036 | 0.035
| 25.5 | 0.046 | 0.045 | 0.044 | 0.042 | 0.042 | 0.04 | 0.04 | 0.039 | 0.038 | 0.037 | 0.037 | 0.036 | 0.035 | 0.035 | 0.034 | 0.033 | 0.033
| 26 | 0.043 | 0.042 | 0.04 | 0.039 | 0.039 | 0.038 | 0.037 | 0.036 | 0.035 | 0.035 | 0.034 | 0.033 | 0.033 | 0.032 | 0.032 | 0.031 | 0.03