## Sheet1
PROPERTIES
General
Name | Nordex N163/5.X Class B 108m 5,5MW
Manufacturer | Nordex
Hub Height | 108
Power
Rated Power | 5500
Peak Power | 5500
Power Regulation Type | Pitch
Voltage | 750
Rotor
Rotor diameter | 163
Number of blades | 3
Rated RPM | 11.8
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 26
Restart Wind Speed | 25.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 45
High Temperature Restart | 40
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | B
Values
Certification | IEC 3rd Edition
Vave | 6.5-8
Vref | 38.8-40.3
Design TI | 0.16

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 12 | 15 | 17 | 19 | 22 | 24 | 26 | 28 | 31 | 33 | 35 | 37 | 40 | 42 | 44 | 46 | 49
| 3.5 | 90 | 95 | 99 | 103 | 108 | 112 | 117 | 121 | 126 | 130 | 134 | 139 | 143 | 148 | 152 | 156 | 161
| 4 | 194 | 201 | 209 | 216 | 223 | 231 | 238 | 245 | 253 | 260 | 267 | 275 | 282 | 289 | 296 | 304 | 311
| 4.5 | 323 | 334 | 345 | 355 | 366 | 377 | 388 | 399 | 410 | 421 | 432 | 442 | 453 | 464 | 475 | 486 | 497
| 5 | 477 | 492 | 507 | 522 | 537 | 552 | 567 | 582 | 598 | 613 | 628 | 643 | 658 | 673 | 688 | 703 | 719
| 5.5 | 659 | 680 | 700 | 720 | 740 | 760 | 781 | 801 | 821 | 841 | 861 | 881 | 902 | 922 | 942 | 962 | 982
| 6 | 876 | 903 | 929 | 955 | 981 | 1007 | 1034 | 1060 | 1086 | 1112 | 1138 | 1164 | 1190 | 1217 | 1243 | 1269 | 1295
| 6.5 | 1132 | 1165 | 1199 | 1232 | 1265 | 1298 | 1332 | 1365 | 1398 | 1431 | 1464 | 1498 | 1531 | 1564 | 1597 | 1630 | 1663
| 7 | 1430 | 1471 | 1513 | 1554 | 1596 | 1637 | 1678 | 1720 | 1761 | 1803 | 1844 | 1885 | 1927 | 1968 | 2009 | 2051 | 2092
| 7.5 | 1773 | 1824 | 1875 | 1926 | 1977 | 2028 | 2078 | 2129 | 2180 | 2231 | 2282 | 2332 | 2383 | 2434 | 2484 | 2535 | 2586
| 8 | 2154 | 2215 | 2277 | 2338 | 2399 | 2460 | 2522 | 2583 | 2644 | 2705 | 2766 | 2827 | 2889 | 2950 | 3011 | 3072 | 3133
| 8.5 | 2547 | 2620 | 2692 | 2764 | 2836 | 2908 | 2980 | 3052 | 3123 | 3195 | 3267 | 3339 | 3411 | 3482 | 3554 | 3626 | 3697
| 9 | 2936 | 3019 | 3102 | 3184 | 3267 | 3350 | 3432 | 3515 | 3597 | 3679 | 3762 | 3844 | 3927 | 4009 | 4091 | 4172 | 4253
| 9.5 | 3309 | 3401 | 3494 | 3587 | 3680 | 3772 | 3865 | 3957 | 4050 | 4144 | 4236 | 4326 | 4415 | 4504 | 4581 | 4649 | 4718
| 10 | 3658 | 3761 | 3863 | 3965 | 4067 | 4170 | 4273 | 4375 | 4472 | 4568 | 4662 | 4736 | 4810 | 4884 | 4946 | 5000 | 5054
| 10.5 | 3988 | 4100 | 4210 | 4323 | 4435 | 4540 | 4643 | 4743 | 4822 | 4902 | 4979 | 5038 | 5097 | 5156 | 5203 | 5243 | 5282
| 11 | 4301 | 4422 | 4543 | 4654 | 4762 | 4853 | 4937 | 5018 | 5082 | 5145 | 5207 | 5250 | 5293 | 5337 | 5370 | 5396 | 5421
| 11.5 | 4601 | 4719 | 4832 | 4926 | 5014 | 5088 | 5155 | 5221 | 5268 | 5315 | 5361 | 5390 | 5418 | 5447 | 5465 | 5475 | 5486
| 12 | 4862 | 4964 | 5057 | 5133 | 5205 | 5261 | 5312 | 5361 | 5393 | 5425 | 5455 | 5468 | 5482 | 5495 | 5500 | 5500 | 5500
| 12.5 | 5070 | 5153 | 5228 | 5288 | 5342 | 5383 | 5418 | 5451 | 5467 | 5483 | 5498 | 5499 | 5499 | 5500 | 5500 | 5500 | 5500
| 13 | 5229 | 5295 | 5353 | 5396 | 5434 | 5459 | 5478 | 5495 | 5497 | 5499 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 13.5 | 5347 | 5395 | 5437 | 5463 | 5486 | 5494 | 5498 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 14 | 5427 | 5459 | 5484 | 5494 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 14.5 | 5476 | 5492 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 15 | 5497 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 15.5 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 16 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 16.5 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 17 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 17.5 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 18 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 18.5 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 19 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 19.5 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 20 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| 20.5 | 5493 | 5493 | 5493 | 5493 | 5493 | 5493 | 5493 | 5493 | 5493 | 5493 | 5493 | 5493 | 5493 | 5493 | 5493 | 5493 | 5493
| 21 | 5427 | 5427 | 5427 | 5427 | 5427 | 5427 | 5427 | 5427 | 5427 | 5427 | 5427 | 5427 | 5427 | 5427 | 5427 | 5427 | 5427
| 21.5 | 5307 | 5307 | 5307 | 5307 | 5307 | 5307 | 5307 | 5307 | 5307 | 5307 | 5307 | 5307 | 5307 | 5307 | 5307 | 5307 | 5307
| 22 | 5153 | 5153 | 5153 | 5153 | 5153 | 5153 | 5153 | 5153 | 5153 | 5153 | 5153 | 5153 | 5153 | 5153 | 5153 | 5153 | 5153
| 22.5 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005
| 23 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856
| 23.5 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708
| 24 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560
| 24.5 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418
| 25 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269
| 25.5 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121
| 26 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764
| 3.5 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208
| 4 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819
| 4.5 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639
| 5 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875
| 5.5 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458
| 6 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181
| 6.5 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042
| 7 | 0.55833 | 0.55833 | 0.55833 | 0.55833 | 0.55833 | 0.55833 | 0.55833 | 0.55833 | 0.55833 | 0.55833 | 0.55833 | 0.55833 | 0.55833 | 0.55833 | 0.55833 | 0.55833 | 0.55833
| 7.5 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54653 | 0.54653
| 8 | 0.52708 | 0.52708 | 0.52708 | 0.52708 | 0.52708 | 0.52708 | 0.52708 | 0.52708 | 0.52708 | 0.52708 | 0.52708 | 0.52708 | 0.52708 | 0.52708 | 0.52708 | 0.52708 | 0.52708
| 8.5 | 0.50278 | 0.50278 | 0.50278 | 0.50278 | 0.50278 | 0.50278 | 0.50278 | 0.50278 | 0.50278 | 0.50278 | 0.50278 | 0.50278 | 0.50278 | 0.50278 | 0.50208 | 0.50139 | 0.50069
| 9 | 0.47569 | 0.47569 | 0.47569 | 0.47569 | 0.47569 | 0.47569 | 0.47569 | 0.47569 | 0.47569 | 0.47569 | 0.47569 | 0.47431 | 0.47292 | 0.47222 | 0.47083 | 0.46875 | 0.46667
| 9.5 | 0.44722 | 0.44722 | 0.44722 | 0.44722 | 0.44722 | 0.44722 | 0.44653 | 0.44653 | 0.44514 | 0.44375 | 0.44306 | 0.44097 | 0.43889 | 0.4375 | 0.43542 | 0.43264 | 0.43056
| 10 | 0.41806 | 0.41806 | 0.41806 | 0.41736 | 0.41736 | 0.41597 | 0.41458 | 0.41389 | 0.41181 | 0.40972 | 0.40833 | 0.40556 | 0.40347 | 0.40139 | 0.39861 | 0.39583 | 0.39306
| 10.5 | 0.38819 | 0.38819 | 0.3875 | 0.38611 | 0.38472 | 0.38333 | 0.38125 | 0.37986 | 0.37708 | 0.375 | 0.37292 | 0.37014 | 0.36736 | 0.36458 | 0.36181 | 0.35903 | 0.35556
| 11 | 0.35764 | 0.35694 | 0.35556 | 0.35347 | 0.35208 | 0.35 | 0.34792 | 0.34514 | 0.34236 | 0.34028 | 0.3375 | 0.33472 | 0.33194 | 0.32917 | 0.32569 | 0.32222 | 0.31944
| 11.5 | 0.32708 | 0.325 | 0.32361 | 0.32153 | 0.31944 | 0.31667 | 0.31389 | 0.31181 | 0.30903 | 0.30625 | 0.30347 | 0.3 | 0.29653 | 0.29375 | 0.29097 | 0.2875 | 0.28403
| 12 | 0.29722 | 0.29514 | 0.29306 | 0.29097 | 0.28889 | 0.28611 | 0.28333 | 0.28056 | 0.27708 | 0.27431 | 0.27153 | 0.26806 | 0.26458 | 0.26181 | 0.25833 | 0.25486 | 0.25139
| 12.5 | 0.27083 | 0.26875 | 0.26667 | 0.26389 | 0.26111 | 0.25833 | 0.25556 | 0.25278 | 0.24931 | 0.24583 | 0.24306 | 0.23958 | 0.23611 | 0.23333 | 0.22986 | 0.22639 | 0.22292
| 13 | 0.24722 | 0.24444 | 0.24236 | 0.23958 | 0.23681 | 0.23333 | 0.23056 | 0.22778 | 0.22431 | 0.22083 | 0.21806 | 0.21458 | 0.21111 | 0.20764 | 0.20417 | 0.20069 | 0.19722
| 13.5 | 0.22569 | 0.22292 | 0.22014 | 0.21736 | 0.21458 | 0.21111 | 0.20833 | 0.20486 | 0.20139 | 0.19861 | 0.19514 | 0.19167 | 0.18819 | 0.18542 | 0.18194 | 0.17847 | 0.175
| 14 | 0.20625 | 0.20347 | 0.20069 | 0.19722 | 0.19444 | 0.19097 | 0.18819 | 0.18472 | 0.18125 | 0.17847 | 0.175 | 0.17153 | 0.16806 | 0.16528 | 0.16181 | 0.15833 | 0.15486
| 14.5 | 0.18819 | 0.18542 | 0.18264 | 0.17917 | 0.17639 | 0.17292 | 0.17014 | 0.16667 | 0.16319 | 0.16042 | 0.15694 | 0.15347 | 0.15 | 0.14722 | 0.14375 | 0.14097 | 0.13819
| 15 | 0.17222 | 0.16944 | 0.16667 | 0.16319 | 0.16042 | 0.15694 | 0.15347 | 0.15069 | 0.14722 | 0.14375 | 0.14097 | 0.1375 | 0.13472 | 0.13194 | 0.12917 | 0.12639 | 0.12431
| 15.5 | 0.15764 | 0.15486 | 0.15139 | 0.14861 | 0.14514 | 0.14236 | 0.13889 | 0.13542 | 0.13264 | 0.12917 | 0.12639 | 0.12361 | 0.12153 | 0.11875 | 0.11667 | 0.11458 | 0.11181
| 16 | 0.14444 | 0.14097 | 0.13819 | 0.13542 | 0.13194 | 0.12847 | 0.12569 | 0.12292 | 0.12014 | 0.11736 | 0.11458 | 0.1125 | 0.10972 | 0.10764 | 0.10556 | 0.10347 | 0.10208
| 16.5 | 0.13264 | 0.12917 | 0.12639 | 0.12292 | 0.12014 | 0.11736 | 0.11458 | 0.11181 | 0.10903 | 0.10694 | 0.10486 | 0.10208 | 0.1 | 0.098611 | 0.096528 | 0.094444 | 0.093056
| 17 | 0.12222 | 0.11875 | 0.11597 | 0.1125 | 0.10972 | 0.10764 | 0.10486 | 0.10278 | 0.1 | 0.097917 | 0.095833 | 0.09375 | 0.092361 | 0.090278 | 0.088889 | 0.086806 | 0.085417
| 17.5 | 0.1125 | 0.10972 | 0.10694 | 0.10417 | 0.10139 | 0.099306 | 0.096528 | 0.094444 | 0.092361 | 0.090278 | 0.088889 | 0.086806 | 0.085417 | 0.083333 | 0.081944 | 0.080556 | 0.079167
| 18 | 0.10486 | 0.10208 | 0.099306 | 0.096528 | 0.094444 | 0.092361 | 0.090278 | 0.088194 | 0.086111 | 0.084028 | 0.082639 | 0.08125 | 0.079167 | 0.077778 | 0.076389 | 0.075 | 0.073611
| 18.5 | 0.097917 | 0.095139 | 0.093056 | 0.090278 | 0.088194 | 0.086111 | 0.084028 | 0.082639 | 0.080556 | 0.079167 | 0.077083 | 0.075694 | 0.074306 | 0.072917 | 0.071528 | 0.070139 | 0.069444
| 19 | 0.091667 | 0.089583 | 0.0875 | 0.085417 | 0.083333 | 0.08125 | 0.079167 | 0.077778 | 0.075694 | 0.074306 | 0.072917 | 0.071528 | 0.070139 | 0.099 | 0.097 | 0.096 | 0.094
| 19.5 | 0.086806 | 0.084722 | 0.082639 | 0.080556 | 0.078472 | 0.077083 | 0.075 | 0.073611 | 0.072222 | 0.070833 | 0.069444 | 0.098 | 0.096 | 0.094 | 0.092 | 0.091 | 0.089
| 20 | 0.082639 | 0.080556 | 0.078472 | 0.077083 | 0.075 | 0.073611 | 0.071528 | 0.070139 | 0.099 | 0.097 | 0.095 | 0.093 | 0.091 | 0.09 | 0.088 | 0.087 | 0.085
| 20.5 | 0.075694 | 0.074306 | 0.072222 | 0.070833 | 0.099 | 0.098 | 0.095 | 0.093 | 0.091 | 0.089 | 0.087 | 0.086 | 0.084 | 0.083 | 0.081 | 0.08 | 0.078
| 21 | 0.069444 | 0.098 | 0.095 | 0.093 | 0.091 | 0.089 | 0.087 | 0.085 | 0.083 | 0.082 | 0.08 | 0.078 | 0.077 | 0.076 | 0.074 | 0.073 | 0.071
| 21.5 | 0.091 | 0.088 | 0.086 | 0.085 | 0.082 | 0.081 | 0.078 | 0.077 | 0.075 | 0.074 | 0.072 | 0.071 | 0.069 | 0.069 | 0.067 | 0.066 | 0.065
| 22 | 0.083 | 0.081 | 0.079 | 0.077 | 0.075 | 0.074 | 0.072 | 0.07 | 0.069 | 0.068 | 0.066 | 0.065 | 0.063 | 0.063 | 0.061 | 0.061 | 0.059
| 22.5 | 0.076 | 0.074 | 0.072 | 0.071 | 0.069 | 0.068 | 0.066 | 0.064 | 0.063 | 0.062 | 0.061 | 0.059 | 0.058 | 0.057 | 0.056 | 0.056 | 0.054
| 23 | 0.07 | 0.068 | 0.066 | 0.065 | 0.063 | 0.062 | 0.06 | 0.059 | 0.058 | 0.057 | 0.056 | 0.054 | 0.053 | 0.053 | 0.052 | 0.051 | 0.05
| 23.5 | 0.063 | 0.062 | 0.06 | 0.059 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053 | 0.052 | 0.05 | 0.049 | 0.048 | 0.048 | 0.047 | 0.046 | 0.045
| 24 | 0.058 | 0.057 | 0.055 | 0.054 | 0.053 | 0.052 | 0.05 | 0.049 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.043 | 0.042
| 24.5 | 0.054 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.046 | 0.045 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.041 | 0.04 | 0.039 | 0.038
| 25 | 0.05 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.04 | 0.039 | 0.038 | 0.038 | 0.037 | 0.036 | 0.035
| 25.5 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.038 | 0.037 | 0.037 | 0.036 | 0.035 | 0.035 | 0.034 | 0.033 | 0.033
| 26 | 0.043 | 0.042 | 0.04 | 0.04 | 0.039 | 0.038 | 0.037 | 0.036 | 0.035 | 0.035 | 0.034 | 0.033 | 0.033 | 0.032 | 0.032 | 0.031 | 0.03