## Sheet1
PROPERTIES
General
Name | Nordex N163/5.X Class B 5,27MW
Manufacturer | Nordex
Hub Height | 118 | 120 | 148 | 159 | 164
Power
Rated Power | 5270
Peak Power | 5270
Power Regulation Type | Pitch
Voltage | 750
Rotor
Rotor diameter | 163
Number of blades | 3
Rated RPM | 11.8
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 26
Restart Wind Speed | 25.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 45
High Temperature Restart | 40
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | B
Values
Certification | IEC 3rd Edition
Vave | 6.5-8
Vref | 38.8-40.3
Design TI | 0.16

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 18 | 21 | 23 | 25 | 28 | 30 | 32 | 34 | 37 | 39 | 41 | 44 | 46 | 48 | 50 | 53 | 55
| 3.5 | 97 | 101 | 106 | 110 | 115 | 119 | 124 | 128 | 133 | 137 | 142 | 146 | 151 | 155 | 159 | 164 | 168
| 4 | 202 | 209 | 217 | 224 | 231 | 239 | 246 | 254 | 261 | 268 | 276 | 283 | 290 | 298 | 305 | 312 | 320
| 4.5 | 332 | 343 | 354 | 365 | 376 | 387 | 398 | 409 | 420 | 431 | 441 | 452 | 463 | 474 | 485 | 496 | 507
| 5 | 487 | 502 | 517 | 533 | 548 | 563 | 578 | 594 | 609 | 624 | 639 | 655 | 670 | 685 | 700 | 716 | 731
| 5.5 | 671 | 692 | 712 | 732 | 753 | 773 | 793 | 814 | 834 | 854 | 875 | 895 | 915 | 936 | 956 | 976 | 997
| 6 | 890 | 916 | 943 | 969 | 996 | 1022 | 1048 | 1075 | 1101 | 1127 | 1154 | 1180 | 1206 | 1232 | 1259 | 1285 | 1311
| 6.5 | 1148 | 1181 | 1214 | 1248 | 1281 | 1315 | 1348 | 1382 | 1415 | 1448 | 1482 | 1515 | 1548 | 1582 | 1615 | 1648 | 1682
| 7 | 1447 | 1489 | 1531 | 1572 | 1614 | 1656 | 1697 | 1739 | 1780 | 1822 | 1864 | 1905 | 1947 | 1988 | 2030 | 2071 | 2113
| 7.5 | 1789 | 1840 | 1891 | 1942 | 1993 | 2043 | 2094 | 2145 | 2196 | 2247 | 2298 | 2349 | 2399 | 2450 | 2501 | 2551 | 2602
| 8 | 2151 | 2212 | 2273 | 2334 | 2394 | 2455 | 2516 | 2577 | 2637 | 2698 | 2759 | 2819 | 2880 | 2940 | 3001 | 3061 | 3122
| 8.5 | 2513 | 2584 | 2655 | 2725 | 2796 | 2866 | 2937 | 3007 | 3078 | 3148 | 3219 | 3289 | 3359 | 3430 | 3500 | 3570 | 3640
| 9 | 2861 | 2942 | 3022 | 3102 | 3182 | 3262 | 3342 | 3422 | 3502 | 3581 | 3661 | 3741 | 3820 | 3900 | 3980 | 4058 | 4136
| 9.5 | 3189 | 3278 | 3367 | 3456 | 3545 | 3634 | 3722 | 3811 | 3900 | 3989 | 4078 | 4165 | 4251 | 4336 | 4421 | 4488 | 4553
| 10 | 3496 | 3593 | 3691 | 3788 | 3885 | 3982 | 4079 | 4177 | 4272 | 4364 | 4455 | 4538 | 4609 | 4679 | 4749 | 4802 | 4853
| 10.5 | 3787 | 3892 | 3997 | 4102 | 4208 | 4313 | 4413 | 4510 | 4599 | 4674 | 4749 | 4816 | 4872 | 4927 | 4983 | 5022 | 5059
| 11 | 4063 | 4175 | 4288 | 4401 | 4505 | 4607 | 4693 | 4772 | 4844 | 4904 | 4963 | 5015 | 5057 | 5098 | 5138 | 5163 | 5187
| 11.5 | 4328 | 4449 | 4559 | 4664 | 4752 | 4835 | 4904 | 4968 | 5024 | 5069 | 5113 | 5151 | 5178 | 5205 | 5232 | 5242 | 5252
| 12 | 4580 | 4689 | 4782 | 4869 | 4940 | 5007 | 5061 | 5109 | 5150 | 5180 | 5210 | 5233 | 5245 | 5258 | 5270 | 5270 | 5270
| 12.5 | 4787 | 4878 | 4954 | 5025 | 5080 | 5131 | 5169 | 5202 | 5229 | 5244 | 5259 | 5268 | 5269 | 5270 | 5270 | 5270 | 5270
| 13 | 4950 | 5023 | 5083 | 5137 | 5177 | 5213 | 5236 | 5254 | 5266 | 5268 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270
| 13.5 | 5072 | 5129 | 5173 | 5212 | 5236 | 5257 | 5266 | 5269 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270
| 14 | 5162 | 5203 | 5232 | 5255 | 5264 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270
| 14.5 | 5223 | 5250 | 5262 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270
| 15 | 5258 | 5268 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270
| 15.5 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270
| 16 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270
| 16.5 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270
| 17 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270
| 17.5 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270
| 18 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270
| 18.5 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270
| 19 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270
| 19.5 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270
| 20 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270
| 20.5 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270
| 21 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270 | 5270
| 21.5 | 5238 | 5238 | 5238 | 5238 | 5238 | 5238 | 5238 | 5238 | 5238 | 5238 | 5238 | 5238 | 5238 | 5238 | 5238 | 5238 | 5238
| 22 | 5150 | 5150 | 5150 | 5150 | 5150 | 5150 | 5150 | 5150 | 5150 | 5150 | 5150 | 5150 | 5150 | 5150 | 5150 | 5150 | 5150
| 22.5 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005 | 5005
| 23 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856 | 4856
| 23.5 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708
| 24 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560
| 24.5 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418
| 25 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269
| 25.5 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121
| 26 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764
| 3.5 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208
| 4 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819
| 4.5 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639
| 5 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875
| 5.5 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458
| 6 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181 | 0.56181
| 6.5 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042 | 0.56042
| 7 | 0.55208 | 0.55208 | 0.55208 | 0.55208 | 0.55208 | 0.55208 | 0.55208 | 0.55208 | 0.55208 | 0.55208 | 0.55208 | 0.55208 | 0.55208 | 0.55208 | 0.55208 | 0.55208 | 0.55208
| 7.5 | 0.53472 | 0.53472 | 0.53472 | 0.53472 | 0.53472 | 0.53472 | 0.53472 | 0.53472 | 0.53472 | 0.53472 | 0.53472 | 0.53472 | 0.53472 | 0.53472 | 0.53472 | 0.53403 | 0.53403
| 8 | 0.51042 | 0.51042 | 0.51042 | 0.51042 | 0.51042 | 0.51042 | 0.51042 | 0.51042 | 0.51042 | 0.51042 | 0.51042 | 0.51042 | 0.51042 | 0.51042 | 0.51042 | 0.51042 | 0.51042
| 8.5 | 0.48333 | 0.48333 | 0.48333 | 0.48333 | 0.48333 | 0.48333 | 0.48333 | 0.48333 | 0.48333 | 0.48333 | 0.48333 | 0.48333 | 0.48333 | 0.48333 | 0.48333 | 0.48194 | 0.48125
| 9 | 0.45347 | 0.45347 | 0.45347 | 0.45347 | 0.45347 | 0.45347 | 0.45347 | 0.45347 | 0.45347 | 0.45347 | 0.45347 | 0.45278 | 0.45208 | 0.45069 | 0.45 | 0.44861 | 0.44653
| 9.5 | 0.42292 | 0.42292 | 0.42292 | 0.42292 | 0.42292 | 0.42292 | 0.42292 | 0.42292 | 0.42222 | 0.42083 | 0.42014 | 0.41875 | 0.41736 | 0.41597 | 0.41389 | 0.41181 | 0.40972
| 10 | 0.39236 | 0.39236 | 0.39236 | 0.39236 | 0.39236 | 0.39167 | 0.39097 | 0.38958 | 0.38819 | 0.38681 | 0.38542 | 0.38333 | 0.38125 | 0.37917 | 0.37708 | 0.37431 | 0.37222
| 10.5 | 0.36181 | 0.36181 | 0.36111 | 0.36042 | 0.35972 | 0.35833 | 0.35694 | 0.35556 | 0.35347 | 0.35139 | 0.35 | 0.34722 | 0.34514 | 0.34236 | 0.34028 | 0.3375 | 0.33472
| 11 | 0.33125 | 0.33056 | 0.32917 | 0.32847 | 0.32708 | 0.325 | 0.32361 | 0.32153 | 0.31944 | 0.31667 | 0.31458 | 0.3125 | 0.30972 | 0.30694 | 0.30417 | 0.30139 | 0.29861
| 11.5 | 0.30208 | 0.30069 | 0.29931 | 0.29792 | 0.29583 | 0.29444 | 0.29167 | 0.28958 | 0.2875 | 0.28472 | 0.28194 | 0.27986 | 0.27639 | 0.27361 | 0.27153 | 0.26806 | 0.26528
| 12 | 0.27569 | 0.27431 | 0.27222 | 0.27014 | 0.26806 | 0.26597 | 0.26389 | 0.26111 | 0.25903 | 0.25625 | 0.25347 | 0.25069 | 0.24722 | 0.24444 | 0.24167 | 0.23889 | 0.23542
| 12.5 | 0.25139 | 0.25 | 0.24792 | 0.24583 | 0.24306 | 0.24097 | 0.23819 | 0.23611 | 0.23333 | 0.22986 | 0.22708 | 0.22431 | 0.22153 | 0.21875 | 0.21597 | 0.2125 | 0.20903
| 13 | 0.22986 | 0.22778 | 0.22569 | 0.22361 | 0.22083 | 0.21806 | 0.21528 | 0.21319 | 0.21042 | 0.20694 | 0.20417 | 0.20139 | 0.19792 | 0.19514 | 0.19236 | 0.18889 | 0.18611
| 13.5 | 0.21042 | 0.20764 | 0.20556 | 0.20347 | 0.20069 | 0.19792 | 0.19514 | 0.19236 | 0.18958 | 0.18681 | 0.18333 | 0.18056 | 0.17778 | 0.17431 | 0.17153 | 0.16806 | 0.16528
| 14 | 0.19236 | 0.19028 | 0.1875 | 0.18472 | 0.18264 | 0.17986 | 0.17708 | 0.17361 | 0.17083 | 0.16806 | 0.16528 | 0.16181 | 0.15903 | 0.15556 | 0.15278 | 0.15 | 0.14653
| 14.5 | 0.17639 | 0.17361 | 0.17083 | 0.16875 | 0.16597 | 0.16319 | 0.16042 | 0.15764 | 0.15417 | 0.15139 | 0.14861 | 0.14514 | 0.14236 | 0.13958 | 0.13681 | 0.13403 | 0.13125
| 15 | 0.16181 | 0.15903 | 0.15625 | 0.15347 | 0.15069 | 0.14792 | 0.14514 | 0.14236 | 0.13958 | 0.13611 | 0.13333 | 0.13056 | 0.12778 | 0.125 | 0.12222 | 0.12014 | 0.11806
| 15.5 | 0.14792 | 0.14583 | 0.14306 | 0.14028 | 0.1375 | 0.13472 | 0.13194 | 0.12847 | 0.12569 | 0.12292 | 0.12014 | 0.11736 | 0.11528 | 0.11319 | 0.11042 | 0.10833 | 0.10625
| 16 | 0.13611 | 0.13333 | 0.13056 | 0.12778 | 0.125 | 0.12222 | 0.11944 | 0.11667 | 0.11389 | 0.11111 | 0.10903 | 0.10694 | 0.10417 | 0.10208 | 0.10069 | 0.098611 | 0.096528
| 16.5 | 0.125 | 0.12222 | 0.11944 | 0.11667 | 0.11389 | 0.11111 | 0.10833 | 0.10625 | 0.10347 | 0.10139 | 0.099306 | 0.097222 | 0.095139 | 0.09375 | 0.091667 | 0.090278 | 0.088194
| 17 | 0.11528 | 0.1125 | 0.10972 | 0.10764 | 0.10486 | 0.10208 | 0.1 | 0.097222 | 0.095139 | 0.093056 | 0.090972 | 0.089583 | 0.0875 | 0.086111 | 0.084028 | 0.082639 | 0.08125
| 17.5 | 0.10694 | 0.10417 | 0.10139 | 0.099306 | 0.096528 | 0.094444 | 0.092361 | 0.090278 | 0.088194 | 0.086111 | 0.084722 | 0.082639 | 0.08125 | 0.079861 | 0.077778 | 0.076389 | 0.075
| 18 | 0.099306 | 0.097222 | 0.094444 | 0.092361 | 0.089583 | 0.0875 | 0.085417 | 0.084028 | 0.081944 | 0.080556 | 0.078472 | 0.077083 | 0.075694 | 0.074306 | 0.072917 | 0.071528 | 0.070139
| 18.5 | 0.093056 | 0.090278 | 0.088194 | 0.086111 | 0.084028 | 0.081944 | 0.080556 | 0.078472 | 0.077083 | 0.075 | 0.073611 | 0.072222 | 0.070833 | 0.069444 | 0.098 | 0.097 | 0.095
| 19 | 0.0875 | 0.085417 | 0.083333 | 0.08125 | 0.079167 | 0.077083 | 0.075694 | 0.074306 | 0.072222 | 0.070833 | 0.069444 | 0.098 | 0.096 | 0.094 | 0.093 | 0.091 | 0.09
| 19.5 | 0.082639 | 0.080556 | 0.078472 | 0.077083 | 0.075 | 0.073611 | 0.071528 | 0.070139 | 0.099 | 0.097 | 0.095 | 0.093 | 0.091 | 0.09 | 0.088 | 0.086 | 0.085
| 20 | 0.079167 | 0.077083 | 0.075 | 0.072917 | 0.071528 | 0.070139 | 0.098 | 0.096 | 0.094 | 0.092 | 0.091 | 0.089 | 0.087 | 0.086 | 0.084 | 0.083 | 0.081
| 20.5 | 0.072917 | 0.070833 | 0.099 | 0.097 | 0.095 | 0.093 | 0.09 | 0.088 | 0.086 | 0.085 | 0.084 | 0.082 | 0.08 | 0.079 | 0.077 | 0.076 | 0.075
| 21 | 0.096 | 0.093 | 0.091 | 0.088 | 0.087 | 0.085 | 0.082 | 0.081 | 0.079 | 0.077 | 0.077 | 0.075 | 0.073 | 0.072 | 0.071 | 0.07 | 0.068
| 21.5 | 0.087 | 0.085 | 0.082 | 0.08 | 0.078 | 0.077 | 0.075 | 0.073 | 0.072 | 0.07 | 0.069 | 0.068 | 0.066 | 0.066 | 0.064 | 0.063 | 0.062
| 22 | 0.079 | 0.077 | 0.075 | 0.073 | 0.072 | 0.07 | 0.068 | 0.067 | 0.066 | 0.064 | 0.063 | 0.062 | 0.061 | 0.06 | 0.059 | 0.058 | 0.056
| 22.5 | 0.073 | 0.071 | 0.069 | 0.067 | 0.066 | 0.064 | 0.063 | 0.061 | 0.06 | 0.059 | 0.058 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053 | 0.052
| 23 | 0.067 | 0.065 | 0.063 | 0.062 | 0.06 | 0.059 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.049 | 0.047
| 23.5 | 0.061 | 0.059 | 0.057 | 0.056 | 0.055 | 0.054 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.046 | 0.045 | 0.044 | 0.043
| 24 | 0.056 | 0.054 | 0.053 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.041 | 0.04
| 24.5 | 0.051 | 0.05 | 0.049 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.041 | 0.04 | 0.039 | 0.039 | 0.038 | 0.037 | 0.036
| 25 | 0.048 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.038 | 0.038 | 0.037 | 0.036 | 0.036 | 0.035 | 0.035 | 0.034
| 25.5 | 0.044 | 0.043 | 0.042 | 0.04 | 0.04 | 0.039 | 0.038 | 0.037 | 0.036 | 0.035 | 0.035 | 0.034 | 0.033 | 0.033 | 0.032 | 0.032 | 0.031
| 26 | 0.041 | 0.04 | 0.039 | 0.038 | 0.037 | 0.036 | 0.035 | 0.034 | 0.034 | 0.033 | 0.033 | 0.032 | 0.031 | 0.031 | 0.03 | 0.03 | 0.029