## Sheet1
PROPERTIES
General
Name | Nordex N163/5.X Class B 4,93MW
Manufacturer | Nordex
Hub Height | 118 | 120 | 164
Power
Rated Power | 4930
Peak Power | 4930
Power Regulation Type | Pitch
Voltage | 750
Rotor
Rotor diameter | 163
Number of blades | 3
Rated RPM | 11.8
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 26
Restart Wind Speed | 25.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 45
High Temperature Restart | 40
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | B
Values
Certification | IEC 3rd Edition
Vave | 6.5-8
Vref | 38.8-40.3
Design TI | 0.16

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 18 | 21 | 23 | 25 | 28 | 30 | 32 | 34 | 37 | 39 | 41 | 44 | 46 | 48 | 50 | 53 | 55
| 3.5 | 97 | 101 | 106 | 110 | 115 | 119 | 124 | 128 | 133 | 137 | 142 | 146 | 151 | 155 | 159 | 164 | 168
| 4 | 202 | 209 | 217 | 224 | 231 | 239 | 246 | 254 | 261 | 268 | 276 | 283 | 290 | 298 | 305 | 312 | 320
| 4.5 | 332 | 343 | 354 | 365 | 376 | 387 | 398 | 409 | 420 | 431 | 441 | 452 | 463 | 474 | 485 | 496 | 507
| 5 | 487 | 502 | 517 | 533 | 548 | 563 | 578 | 594 | 609 | 624 | 639 | 655 | 670 | 685 | 700 | 716 | 731
| 5.5 | 671 | 692 | 712 | 732 | 753 | 773 | 793 | 814 | 834 | 854 | 875 | 895 | 915 | 936 | 956 | 976 | 997
| 6 | 890 | 916 | 943 | 969 | 995 | 1022 | 1048 | 1075 | 1101 | 1127 | 1154 | 1180 | 1206 | 1232 | 1259 | 1285 | 1311
| 6.5 | 1148 | 1181 | 1215 | 1248 | 1282 | 1315 | 1348 | 1382 | 1415 | 1449 | 1482 | 1515 | 1549 | 1582 | 1615 | 1649 | 1682
| 7 | 1445 | 1486 | 1528 | 1570 | 1611 | 1653 | 1694 | 1736 | 1777 | 1819 | 1860 | 1902 | 1943 | 1985 | 2026 | 2067 | 2109
| 7.5 | 1763 | 1813 | 1863 | 1914 | 1964 | 2014 | 2064 | 2114 | 2165 | 2215 | 2265 | 2315 | 2365 | 2415 | 2465 | 2515 | 2565
| 8 | 2080 | 2139 | 2198 | 2257 | 2316 | 2375 | 2434 | 2492 | 2551 | 2610 | 2669 | 2727 | 2786 | 2844 | 2903 | 2962 | 3020
| 8.5 | 2384 | 2451 | 2518 | 2585 | 2653 | 2720 | 2787 | 2854 | 2921 | 2988 | 3055 | 3121 | 3188 | 3255 | 3322 | 3389 | 3455
| 9 | 2668 | 2743 | 2818 | 2893 | 2967 | 3042 | 3117 | 3192 | 3266 | 3341 | 3415 | 3490 | 3564 | 3639 | 3713 | 3788 | 3862
| 9.5 | 2934 | 3016 | 3098 | 3180 | 3262 | 3344 | 3426 | 3508 | 3589 | 3671 | 3753 | 3835 | 3917 | 3997 | 4076 | 4154 | 4226
| 10 | 3185 | 3273 | 3362 | 3451 | 3540 | 3629 | 3717 | 3805 | 3894 | 3983 | 4071 | 4155 | 4239 | 4311 | 4375 | 4440 | 4498
| 10.5 | 3423 | 3518 | 3614 | 3709 | 3804 | 3899 | 3995 | 4091 | 4181 | 4269 | 4352 | 4420 | 4488 | 4546 | 4597 | 4648 | 4693
| 11 | 3654 | 3756 | 3857 | 3959 | 4061 | 4163 | 4256 | 4347 | 4425 | 4497 | 4564 | 4618 | 4672 | 4717 | 4754 | 4791 | 4823
| 11.5 | 3882 | 3990 | 4098 | 4206 | 4301 | 4396 | 4473 | 4548 | 4610 | 4668 | 4721 | 4761 | 4801 | 4832 | 4857 | 4882 | 4900
| 12 | 4108 | 4222 | 4322 | 4420 | 4498 | 4576 | 4638 | 4698 | 4747 | 4790 | 4829 | 4856 | 4883 | 4901 | 4912 | 4923 | 4930
| 12.5 | 4321 | 4421 | 4505 | 4586 | 4650 | 4713 | 4760 | 4806 | 4840 | 4870 | 4895 | 4909 | 4923 | 4929 | 4929 | 4930 | 4930
| 13 | 4496 | 4580 | 4648 | 4715 | 4763 | 4812 | 4845 | 4877 | 4898 | 4914 | 4927 | 4928 | 4930 | 4930 | 4930 | 4930 | 4930
| 13.5 | 4636 | 4706 | 4759 | 4810 | 4845 | 4879 | 4899 | 4918 | 4926 | 4929 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930
| 14 | 4746 | 4801 | 4839 | 4877 | 4898 | 4919 | 4925 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930
| 14.5 | 4829 | 4868 | 4894 | 4917 | 4924 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930
| 15 | 4885 | 4911 | 4922 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930
| 15.5 | 4918 | 4929 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930
| 16 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930
| 16.5 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930
| 17 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930
| 17.5 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930
| 18 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930
| 18.5 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930
| 19 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930
| 19.5 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930
| 20 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930
| 20.5 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930
| 21 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930
| 21.5 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930
| 22 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930
| 22.5 | 4913 | 4913 | 4913 | 4913 | 4913 | 4913 | 4913 | 4913 | 4913 | 4913 | 4913 | 4913 | 4913 | 4913 | 4913 | 4913 | 4913
| 23 | 4838 | 4838 | 4838 | 4838 | 4838 | 4838 | 4838 | 4838 | 4838 | 4838 | 4838 | 4838 | 4838 | 4838 | 4838 | 4838 | 4838
| 23.5 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708
| 24 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560
| 24.5 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418
| 25 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269
| 25.5 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121
| 26 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764
| 3.5 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208
| 4 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819
| 4.5 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639
| 5 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875
| 5.5 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458
| 6 | 0.5625 | 0.5625 | 0.5625 | 0.5625 | 0.5625 | 0.5625 | 0.5625 | 0.5625 | 0.5625 | 0.5625 | 0.5625 | 0.5625 | 0.5625 | 0.5625 | 0.5625 | 0.5625 | 0.5625
| 6.5 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417
| 7 | 0.53542 | 0.53542 | 0.53542 | 0.53542 | 0.53542 | 0.53542 | 0.53542 | 0.53542 | 0.53542 | 0.53542 | 0.53542 | 0.53542 | 0.53542 | 0.53542 | 0.53542 | 0.53542 | 0.53542
| 7.5 | 0.50972 | 0.50972 | 0.50972 | 0.50972 | 0.50972 | 0.50972 | 0.50972 | 0.50972 | 0.50972 | 0.50972 | 0.50972 | 0.50972 | 0.50972 | 0.50972 | 0.50972 | 0.50972 | 0.50972
| 8 | 0.47986 | 0.47986 | 0.47986 | 0.47986 | 0.47986 | 0.47986 | 0.47986 | 0.47986 | 0.47986 | 0.47986 | 0.47986 | 0.48056 | 0.48056 | 0.47986 | 0.47986 | 0.47986 | 0.47986
| 8.5 | 0.44861 | 0.44861 | 0.44861 | 0.44861 | 0.44861 | 0.44861 | 0.44861 | 0.44861 | 0.44861 | 0.44861 | 0.44861 | 0.44861 | 0.44861 | 0.44861 | 0.44861 | 0.44861 | 0.44792
| 9 | 0.41597 | 0.41597 | 0.41597 | 0.41597 | 0.41597 | 0.41597 | 0.41597 | 0.41597 | 0.41597 | 0.41597 | 0.41597 | 0.41597 | 0.41528 | 0.41528 | 0.41458 | 0.41319 | 0.4125
| 9.5 | 0.38264 | 0.38264 | 0.38264 | 0.38264 | 0.38264 | 0.38264 | 0.38264 | 0.38264 | 0.38264 | 0.38264 | 0.38194 | 0.38125 | 0.38056 | 0.37917 | 0.37778 | 0.37639 | 0.375
| 10 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.34931 | 0.34861 | 0.34792 | 0.34653 | 0.34514 | 0.34444 | 0.34236 | 0.34097 | 0.33889 | 0.3375
| 10.5 | 0.31875 | 0.31875 | 0.31875 | 0.31875 | 0.31806 | 0.31806 | 0.31667 | 0.31597 | 0.31458 | 0.31389 | 0.3125 | 0.31042 | 0.30903 | 0.30694 | 0.30486 | 0.30278 | 0.30069
| 11 | 0.29097 | 0.29097 | 0.29028 | 0.29028 | 0.28889 | 0.28819 | 0.28681 | 0.28542 | 0.28403 | 0.28264 | 0.28056 | 0.27847 | 0.27708 | 0.275 | 0.27222 | 0.27014 | 0.26806
| 11.5 | 0.26667 | 0.26597 | 0.26458 | 0.26389 | 0.2625 | 0.26111 | 0.25972 | 0.25833 | 0.25625 | 0.25486 | 0.25278 | 0.25069 | 0.24861 | 0.24583 | 0.24375 | 0.24167 | 0.23889
| 12 | 0.24375 | 0.24306 | 0.24167 | 0.24028 | 0.23889 | 0.2375 | 0.23542 | 0.23403 | 0.23194 | 0.22986 | 0.22778 | 0.225 | 0.22292 | 0.22083 | 0.21806 | 0.21597 | 0.21319
| 12.5 | 0.22361 | 0.22222 | 0.22083 | 0.21944 | 0.21736 | 0.21528 | 0.21389 | 0.21181 | 0.20972 | 0.20764 | 0.20556 | 0.20278 | 0.20069 | 0.19792 | 0.19514 | 0.19306 | 0.19028
| 13 | 0.20486 | 0.20347 | 0.20139 | 0.2 | 0.19792 | 0.19583 | 0.19375 | 0.19167 | 0.18958 | 0.1875 | 0.18542 | 0.18264 | 0.18056 | 0.17778 | 0.175 | 0.17292 | 0.17014
| 13.5 | 0.18819 | 0.18611 | 0.18472 | 0.18264 | 0.18056 | 0.17847 | 0.17639 | 0.17431 | 0.17222 | 0.16944 | 0.16736 | 0.16458 | 0.1625 | 0.15972 | 0.15694 | 0.15486 | 0.15208
| 14 | 0.17292 | 0.17083 | 0.16875 | 0.16667 | 0.16458 | 0.1625 | 0.16042 | 0.15833 | 0.15556 | 0.15347 | 0.15139 | 0.14861 | 0.14583 | 0.14375 | 0.14097 | 0.13819 | 0.13611
| 14.5 | 0.15903 | 0.15694 | 0.15486 | 0.15278 | 0.15069 | 0.14861 | 0.14583 | 0.14375 | 0.14167 | 0.13889 | 0.13681 | 0.13403 | 0.13125 | 0.12917 | 0.12639 | 0.12361 | 0.12153
| 15 | 0.14583 | 0.14375 | 0.14167 | 0.13958 | 0.1375 | 0.13542 | 0.13264 | 0.13056 | 0.12847 | 0.12569 | 0.12361 | 0.12083 | 0.11875 | 0.11597 | 0.11389 | 0.11111 | 0.10903
| 15.5 | 0.13472 | 0.13264 | 0.12986 | 0.12778 | 0.12569 | 0.12361 | 0.12083 | 0.11875 | 0.11667 | 0.11389 | 0.11181 | 0.10903 | 0.10694 | 0.10486 | 0.10278 | 0.10069 | 0.098611
| 16 | 0.12361 | 0.12153 | 0.11944 | 0.11736 | 0.11528 | 0.11319 | 0.11042 | 0.10833 | 0.10556 | 0.10347 | 0.10139 | 0.099306 | 0.097222 | 0.095139 | 0.093056 | 0.091667 | 0.089583
| 16.5 | 0.11458 | 0.1125 | 0.11042 | 0.10833 | 0.10556 | 0.10347 | 0.10069 | 0.098611 | 0.096528 | 0.094444 | 0.092361 | 0.090278 | 0.088889 | 0.086806 | 0.085417 | 0.083333 | 0.081944
| 17 | 0.10625 | 0.10417 | 0.10208 | 0.099306 | 0.097222 | 0.095139 | 0.093056 | 0.090278 | 0.088889 | 0.086806 | 0.084722 | 0.083333 | 0.08125 | 0.079861 | 0.078472 | 0.077083 | 0.075694
| 17.5 | 0.099306 | 0.096528 | 0.094444 | 0.092361 | 0.089583 | 0.0875 | 0.085417 | 0.084028 | 0.081944 | 0.080556 | 0.078472 | 0.077083 | 0.075694 | 0.074306 | 0.072917 | 0.071528 | 0.070139
| 18 | 0.092361 | 0.090278 | 0.088194 | 0.085417 | 0.083333 | 0.081944 | 0.079861 | 0.077778 | 0.076389 | 0.075 | 0.072917 | 0.071528 | 0.070139 | 0.099 | 0.098 | 0.096 | 0.094
| 18.5 | 0.086806 | 0.084722 | 0.081944 | 0.080556 | 0.078472 | 0.076389 | 0.075 | 0.072917 | 0.071528 | 0.070139 | 0.099 | 0.097 | 0.095 | 0.093 | 0.092 | 0.09 | 0.088
| 19 | 0.081944 | 0.079167 | 0.077778 | 0.075694 | 0.073611 | 0.072222 | 0.070139 | 0.099 | 0.097 | 0.095 | 0.093 | 0.091 | 0.09 | 0.088 | 0.086 | 0.085 | 0.083
| 19.5 | 0.077083 | 0.075 | 0.073611 | 0.071528 | 0.070139 | 0.098 | 0.096 | 0.094 | 0.092 | 0.09 | 0.088 | 0.087 | 0.085 | 0.084 | 0.082 | 0.081 | 0.079
| 20 | 0.073611 | 0.071528 | 0.070139 | 0.098 | 0.096 | 0.094 | 0.092 | 0.09 | 0.088 | 0.086 | 0.084 | 0.083 | 0.081 | 0.08 | 0.078 | 0.077 | 0.076
| 20.5 | 0.098 | 0.095 | 0.093 | 0.09 | 0.088 | 0.086 | 0.085 | 0.083 | 0.081 | 0.079 | 0.077 | 0.076 | 0.075 | 0.074 | 0.072 | 0.071 | 0.07
| 21 | 0.089 | 0.087 | 0.085 | 0.082 | 0.081 | 0.079 | 0.077 | 0.076 | 0.074 | 0.072 | 0.071 | 0.07 | 0.068 | 0.067 | 0.066 | 0.065 | 0.064
| 21.5 | 0.081 | 0.078 | 0.077 | 0.075 | 0.073 | 0.072 | 0.07 | 0.069 | 0.067 | 0.066 | 0.064 | 0.063 | 0.062 | 0.061 | 0.059 | 0.059 | 0.058
| 22 | 0.074 | 0.072 | 0.07 | 0.068 | 0.067 | 0.066 | 0.064 | 0.063 | 0.061 | 0.06 | 0.059 | 0.058 | 0.056 | 0.056 | 0.054 | 0.054 | 0.053
| 22.5 | 0.068 | 0.066 | 0.064 | 0.063 | 0.061 | 0.06 | 0.059 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048
| 23 | 0.062 | 0.06 | 0.059 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053 | 0.052 | 0.05 | 0.049 | 0.049 | 0.047 | 0.047 | 0.046 | 0.045 | 0.045
| 23.5 | 0.056 | 0.055 | 0.054 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.041 | 0.04
| 24 | 0.052 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.041 | 0.04 | 0.039 | 0.038 | 0.038 | 0.037
| 24.5 | 0.048 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.041 | 0.04 | 0.039 | 0.038 | 0.037 | 0.036 | 0.036 | 0.035 | 0.035 | 0.034
| 25 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.038 | 0.038 | 0.037 | 0.036 | 0.035 | 0.035 | 0.034 | 0.033 | 0.033 | 0.032 | 0.032
| 25.5 | 0.041 | 0.04 | 0.039 | 0.038 | 0.037 | 0.036 | 0.035 | 0.035 | 0.034 | 0.033 | 0.032 | 0.032 | 0.031 | 0.031 | 0.03 | 0.03 | 0.029
| 26 | 0.038 | 0.037 | 0.036 | 0.035 | 0.034 | 0.034 | 0.033 | 0.032 | 0.032 | 0.031 | 0.03 | 0.03 | 0.029 | 0.029 | 0.028 | 0.028 | 0.027