## Sheet1
PROPERTIES
General
Name | Nordex N163/5.X Class B 108m 4,93MW
Manufacturer | Nordex
Hub Height | 108
Power
Rated Power | 4930
Peak Power | 4930
Power Regulation Type | Pitch
Voltage | 750
Rotor
Rotor diameter | 163
Number of blades | 3
Rated RPM | 11.8
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 26
Restart Wind Speed | 25.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 45
High Temperature Restart | 40
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | B
Values
Certification | IEC 3rd Edition
Vave | 6.5-8
Vref | 38.8-40.3
Design TI | 0.16

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 12 | 15 | 17 | 19 | 22 | 24 | 26 | 28 | 31 | 33 | 35 | 37 | 40 | 42 | 44 | 46 | 49
| 3.5 | 90 | 95 | 99 | 103 | 108 | 112 | 117 | 121 | 126 | 130 | 134 | 139 | 143 | 148 | 152 | 156 | 161
| 4 | 194 | 201 | 209 | 216 | 223 | 231 | 238 | 245 | 253 | 260 | 267 | 275 | 282 | 289 | 296 | 304 | 311
| 4.5 | 323 | 334 | 345 | 355 | 366 | 377 | 388 | 399 | 410 | 421 | 432 | 442 | 453 | 464 | 475 | 486 | 497
| 5 | 477 | 492 | 507 | 522 | 537 | 552 | 567 | 582 | 598 | 613 | 628 | 643 | 658 | 673 | 688 | 703 | 719
| 5.5 | 659 | 680 | 700 | 720 | 740 | 760 | 781 | 801 | 821 | 841 | 861 | 881 | 902 | 922 | 942 | 962 | 982
| 6 | 876 | 903 | 929 | 955 | 981 | 1007 | 1034 | 1060 | 1086 | 1112 | 1138 | 1164 | 1190 | 1217 | 1243 | 1269 | 1295
| 6.5 | 1132 | 1166 | 1199 | 1232 | 1265 | 1299 | 1332 | 1365 | 1398 | 1431 | 1465 | 1498 | 1531 | 1564 | 1597 | 1630 | 1664
| 7 | 1428 | 1469 | 1510 | 1552 | 1593 | 1634 | 1676 | 1717 | 1758 | 1800 | 1841 | 1882 | 1923 | 1965 | 2006 | 2047 | 2088
| 7.5 | 1744 | 1794 | 1844 | 1894 | 1944 | 1994 | 2044 | 2094 | 2144 | 2194 | 2244 | 2294 | 2344 | 2394 | 2444 | 2494 | 2543
| 8 | 2060 | 2119 | 2177 | 2236 | 2295 | 2353 | 2412 | 2471 | 2529 | 2588 | 2646 | 2705 | 2764 | 2822 | 2881 | 2939 | 2997
| 8.5 | 2362 | 2429 | 2496 | 2563 | 2630 | 2697 | 2764 | 2831 | 2898 | 2965 | 3032 | 3099 | 3165 | 3232 | 3299 | 3365 | 3432
| 9 | 2646 | 2720 | 2795 | 2870 | 2945 | 3019 | 3094 | 3169 | 3243 | 3318 | 3392 | 3467 | 3541 | 3615 | 3690 | 3765 | 3839
| 9.5 | 2911 | 2993 | 3075 | 3157 | 3239 | 3321 | 3403 | 3484 | 3566 | 3648 | 3729 | 3812 | 3894 | 3975 | 4054 | 4132 | 4208
| 10 | 3161 | 3250 | 3339 | 3428 | 3517 | 3605 | 3694 | 3782 | 3871 | 3960 | 4049 | 4133 | 4217 | 4293 | 4358 | 4423 | 4485
| 10.5 | 3400 | 3495 | 3591 | 3686 | 3781 | 3876 | 3972 | 4068 | 4160 | 4248 | 4335 | 4403 | 4471 | 4533 | 4584 | 4635 | 4684
| 11 | 3631 | 3733 | 3834 | 3936 | 4038 | 4140 | 4235 | 4327 | 4408 | 4480 | 4551 | 4605 | 4659 | 4707 | 4745 | 4782 | 4817
| 11.5 | 3859 | 3967 | 4075 | 4184 | 4281 | 4376 | 4456 | 4531 | 4597 | 4655 | 4711 | 4752 | 4792 | 4826 | 4851 | 4876 | 4898
| 12 | 4086 | 4200 | 4302 | 4400 | 4482 | 4560 | 4625 | 4686 | 4737 | 4781 | 4823 | 4850 | 4877 | 4898 | 4910 | 4921 | 4930
| 12.5 | 4301 | 4402 | 4489 | 4570 | 4637 | 4700 | 4750 | 4796 | 4834 | 4864 | 4892 | 4906 | 4920 | 4929 | 4929 | 4930 | 4930
| 13 | 4480 | 4565 | 4636 | 4702 | 4754 | 4802 | 4839 | 4871 | 4895 | 4911 | 4926 | 4928 | 4930 | 4930 | 4930 | 4930 | 4930
| 13.5 | 4624 | 4693 | 4749 | 4801 | 4838 | 4873 | 4896 | 4914 | 4925 | 4928 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930
| 14 | 4737 | 4791 | 4833 | 4870 | 4894 | 4915 | 4924 | 4929 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930
| 14.5 | 4822 | 4862 | 4890 | 4913 | 4923 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930
| 15 | 4881 | 4907 | 4920 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930
| 15.5 | 4916 | 4927 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930
| 16 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930
| 16.5 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930
| 17 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930
| 17.5 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930
| 18 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930
| 18.5 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930
| 19 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930
| 19.5 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930
| 20 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930
| 20.5 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930
| 21 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930
| 21.5 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930
| 22 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930 | 4930
| 22.5 | 4913 | 4913 | 4913 | 4913 | 4913 | 4913 | 4913 | 4913 | 4913 | 4913 | 4913 | 4913 | 4913 | 4913 | 4913 | 4913 | 4913
| 23 | 4838 | 4838 | 4838 | 4838 | 4838 | 4838 | 4838 | 4838 | 4838 | 4838 | 4838 | 4838 | 4838 | 4838 | 4838 | 4838 | 4838
| 23.5 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708 | 4708
| 24 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560
| 24.5 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418
| 25 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269
| 25.5 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121
| 26 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764
| 3.5 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208
| 4 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819
| 4.5 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639
| 5 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875
| 5.5 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458
| 6 | 0.5625 | 0.5625 | 0.5625 | 0.5625 | 0.5625 | 0.5625 | 0.5625 | 0.5625 | 0.5625 | 0.5625 | 0.5625 | 0.5625 | 0.5625 | 0.5625 | 0.5625 | 0.5625 | 0.5625
| 6.5 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417 | 0.55417
| 7 | 0.53542 | 0.53542 | 0.53542 | 0.53542 | 0.53542 | 0.53542 | 0.53542 | 0.53542 | 0.53542 | 0.53542 | 0.53542 | 0.53542 | 0.53542 | 0.53542 | 0.53542 | 0.53542 | 0.53542
| 7.5 | 0.50972 | 0.50972 | 0.50972 | 0.50972 | 0.50972 | 0.50972 | 0.50972 | 0.50972 | 0.50972 | 0.50972 | 0.50972 | 0.50972 | 0.50972 | 0.50972 | 0.50972 | 0.50972 | 0.50972
| 8 | 0.47986 | 0.47986 | 0.47986 | 0.47986 | 0.47986 | 0.47986 | 0.47986 | 0.47986 | 0.47986 | 0.47986 | 0.47986 | 0.48056 | 0.48056 | 0.48056 | 0.47986 | 0.47986 | 0.47986
| 8.5 | 0.44861 | 0.44861 | 0.44861 | 0.44861 | 0.44861 | 0.44861 | 0.44861 | 0.44861 | 0.44861 | 0.44861 | 0.44861 | 0.44861 | 0.44861 | 0.44861 | 0.44861 | 0.44861 | 0.44861
| 9 | 0.41597 | 0.41597 | 0.41597 | 0.41597 | 0.41597 | 0.41597 | 0.41597 | 0.41597 | 0.41597 | 0.41597 | 0.41597 | 0.41597 | 0.41528 | 0.41528 | 0.41458 | 0.41389 | 0.4125
| 9.5 | 0.38264 | 0.38264 | 0.38264 | 0.38264 | 0.38264 | 0.38264 | 0.38264 | 0.38264 | 0.38264 | 0.38264 | 0.38194 | 0.38125 | 0.38056 | 0.37986 | 0.37847 | 0.37708 | 0.37569
| 10 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.34931 | 0.34861 | 0.34792 | 0.34722 | 0.34583 | 0.34444 | 0.34306 | 0.34097 | 0.33958 | 0.3375
| 10.5 | 0.31875 | 0.31875 | 0.31875 | 0.31875 | 0.31806 | 0.31806 | 0.31736 | 0.31597 | 0.31528 | 0.31389 | 0.3125 | 0.31111 | 0.30903 | 0.30764 | 0.30556 | 0.30347 | 0.30139
| 11 | 0.29097 | 0.29097 | 0.29028 | 0.29028 | 0.28889 | 0.28819 | 0.28681 | 0.28611 | 0.28403 | 0.28264 | 0.28125 | 0.27917 | 0.27708 | 0.275 | 0.27292 | 0.27083 | 0.26875
| 11.5 | 0.26667 | 0.26597 | 0.26528 | 0.26389 | 0.26319 | 0.26181 | 0.26042 | 0.25833 | 0.25694 | 0.25486 | 0.25347 | 0.25069 | 0.24861 | 0.24653 | 0.24444 | 0.24167 | 0.23958
| 12 | 0.24375 | 0.24306 | 0.24167 | 0.24028 | 0.23889 | 0.2375 | 0.23611 | 0.23403 | 0.23194 | 0.22986 | 0.22778 | 0.22569 | 0.22361 | 0.22153 | 0.21875 | 0.21597 | 0.21389
| 12.5 | 0.22361 | 0.22222 | 0.22083 | 0.21944 | 0.21736 | 0.21597 | 0.21389 | 0.21181 | 0.20972 | 0.20764 | 0.20556 | 0.20347 | 0.20069 | 0.19861 | 0.19583 | 0.19375 | 0.19097
| 13 | 0.20486 | 0.20347 | 0.20208 | 0.2 | 0.19861 | 0.19653 | 0.19444 | 0.19236 | 0.19028 | 0.18819 | 0.18542 | 0.18333 | 0.18056 | 0.17847 | 0.17569 | 0.17292 | 0.17083
| 13.5 | 0.18819 | 0.18681 | 0.18472 | 0.18264 | 0.18125 | 0.17917 | 0.17708 | 0.17431 | 0.17222 | 0.17014 | 0.16806 | 0.16528 | 0.1625 | 0.16042 | 0.15764 | 0.15486 | 0.15278
| 14 | 0.17292 | 0.17083 | 0.16944 | 0.16736 | 0.16528 | 0.16319 | 0.16111 | 0.15833 | 0.15625 | 0.15417 | 0.15139 | 0.14931 | 0.14653 | 0.14444 | 0.14167 | 0.13889 | 0.13611
| 14.5 | 0.15903 | 0.15694 | 0.15486 | 0.15278 | 0.15069 | 0.14861 | 0.14653 | 0.14444 | 0.14167 | 0.13958 | 0.13681 | 0.13472 | 0.13194 | 0.12986 | 0.12708 | 0.12431 | 0.12222
| 15 | 0.14653 | 0.14444 | 0.14236 | 0.14028 | 0.13819 | 0.13542 | 0.13333 | 0.13125 | 0.12847 | 0.12639 | 0.12431 | 0.12153 | 0.11875 | 0.11667 | 0.11389 | 0.11181 | 0.10972
| 15.5 | 0.13472 | 0.13264 | 0.13056 | 0.12847 | 0.12639 | 0.12361 | 0.12153 | 0.11944 | 0.11667 | 0.11458 | 0.11181 | 0.10972 | 0.10764 | 0.10486 | 0.10278 | 0.10139 | 0.099306
| 16 | 0.12431 | 0.12222 | 0.12014 | 0.11806 | 0.11528 | 0.11319 | 0.11111 | 0.10833 | 0.10625 | 0.10417 | 0.10139 | 0.099306 | 0.097222 | 0.095833 | 0.09375 | 0.091667 | 0.090278
| 16.5 | 0.11458 | 0.1125 | 0.11042 | 0.10833 | 0.10625 | 0.10347 | 0.10139 | 0.099306 | 0.096528 | 0.094444 | 0.093056 | 0.090972 | 0.088889 | 0.0875 | 0.085417 | 0.084028 | 0.082639
| 17 | 0.10694 | 0.10417 | 0.10208 | 0.1 | 0.097917 | 0.095139 | 0.093056 | 0.090972 | 0.088889 | 0.086806 | 0.085417 | 0.083333 | 0.081944 | 0.080556 | 0.078472 | 0.077083 | 0.075694
| 17.5 | 0.099306 | 0.097222 | 0.095139 | 0.092361 | 0.090278 | 0.088194 | 0.086111 | 0.084028 | 0.082639 | 0.080556 | 0.079167 | 0.077083 | 0.075694 | 0.074306 | 0.072917 | 0.071528 | 0.070139
| 18 | 0.093056 | 0.090278 | 0.088194 | 0.086111 | 0.084028 | 0.081944 | 0.079861 | 0.078472 | 0.076389 | 0.075 | 0.073611 | 0.072222 | 0.070833 | 0.069444 | 0.098 | 0.096 | 0.094
| 18.5 | 0.086806 | 0.084722 | 0.082639 | 0.080556 | 0.078472 | 0.077083 | 0.075 | 0.073611 | 0.071528 | 0.070139 | 0.099 | 0.097 | 0.095 | 0.094 | 0.092 | 0.09 | 0.089
| 19 | 0.081944 | 0.079861 | 0.077778 | 0.075694 | 0.074306 | 0.072222 | 0.070833 | 0.069444 | 0.098 | 0.095 | 0.094 | 0.092 | 0.09 | 0.088 | 0.087 | 0.085 | 0.084
| 19.5 | 0.077778 | 0.075694 | 0.073611 | 0.072222 | 0.070139 | 0.099 | 0.097 | 0.094 | 0.092 | 0.091 | 0.089 | 0.087 | 0.085 | 0.084 | 0.082 | 0.081 | 0.079
| 20 | 0.073611 | 0.072222 | 0.070139 | 0.099 | 0.096 | 0.094 | 0.092 | 0.09 | 0.088 | 0.086 | 0.085 | 0.083 | 0.082 | 0.08 | 0.079 | 0.077 | 0.076
| 20.5 | 0.098 | 0.096 | 0.093 | 0.091 | 0.088 | 0.086 | 0.085 | 0.083 | 0.081 | 0.079 | 0.078 | 0.076 | 0.075 | 0.074 | 0.073 | 0.071 | 0.07
| 21 | 0.089 | 0.087 | 0.085 | 0.083 | 0.081 | 0.079 | 0.077 | 0.076 | 0.074 | 0.072 | 0.071 | 0.07 | 0.069 | 0.067 | 0.066 | 0.065 | 0.064
| 21.5 | 0.081 | 0.079 | 0.077 | 0.075 | 0.073 | 0.072 | 0.07 | 0.069 | 0.067 | 0.066 | 0.065 | 0.063 | 0.062 | 0.061 | 0.06 | 0.059 | 0.058
| 22 | 0.074 | 0.072 | 0.07 | 0.069 | 0.067 | 0.066 | 0.064 | 0.063 | 0.061 | 0.06 | 0.059 | 0.058 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053
| 22.5 | 0.068 | 0.066 | 0.064 | 0.063 | 0.061 | 0.06 | 0.059 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048
| 23 | 0.062 | 0.061 | 0.059 | 0.058 | 0.056 | 0.055 | 0.054 | 0.053 | 0.052 | 0.05 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.045
| 23.5 | 0.056 | 0.055 | 0.054 | 0.053 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.044 | 0.042 | 0.042 | 0.041 | 0.04
| 24 | 0.052 | 0.051 | 0.049 | 0.049 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.038 | 0.037
| 24.5 | 0.048 | 0.047 | 0.045 | 0.045 | 0.043 | 0.042 | 0.041 | 0.041 | 0.04 | 0.039 | 0.038 | 0.037 | 0.037 | 0.036 | 0.036 | 0.035 | 0.034
| 25 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.038 | 0.038 | 0.037 | 0.036 | 0.035 | 0.035 | 0.034 | 0.033 | 0.033 | 0.032 | 0.032
| 25.5 | 0.041 | 0.04 | 0.039 | 0.038 | 0.037 | 0.036 | 0.035 | 0.035 | 0.034 | 0.033 | 0.033 | 0.032 | 0.032 | 0.031 | 0.03 | 0.03 | 0.029
| 26 | 0.038 | 0.037 | 0.036 | 0.035 | 0.034 | 0.034 | 0.033 | 0.032 | 0.032 | 0.031 | 0.03 | 0.03 | 0.029 | 0.029 | 0.028 | 0.028 | 0.027