## Sheet1
PROPERTIES
General
Name | Nordex N163/5.X Class B 4,81MW
Manufacturer | Nordex
Hub Height | 118 | 120 | 164
Power
Rated Power | 4810
Peak Power | 4810
Power Regulation Type | Pitch
Voltage | 750
Rotor
Rotor diameter | 163
Number of blades | 3
Rated RPM | 11.8
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 26
Restart Wind Speed | 25.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 45
High Temperature Restart | 40
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | B
Values
Certification | IEC 3rd Edition
Vave | 6.5-8
Vref | 38.8-40.3
Design TI | 0.16

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 18 | 21 | 23 | 25 | 28 | 30 | 32 | 34 | 37 | 39 | 41 | 44 | 46 | 48 | 50 | 53 | 55
| 3.5 | 97 | 101 | 106 | 110 | 115 | 119 | 124 | 128 | 133 | 137 | 142 | 146 | 151 | 155 | 159 | 164 | 168
| 4 | 202 | 209 | 217 | 224 | 231 | 239 | 246 | 254 | 261 | 268 | 276 | 283 | 290 | 298 | 305 | 312 | 320
| 4.5 | 332 | 343 | 354 | 365 | 376 | 387 | 398 | 409 | 420 | 431 | 441 | 452 | 463 | 474 | 485 | 496 | 507
| 5 | 487 | 502 | 517 | 533 | 548 | 563 | 578 | 594 | 609 | 624 | 639 | 655 | 670 | 685 | 700 | 716 | 731
| 5.5 | 671 | 692 | 712 | 732 | 753 | 773 | 793 | 814 | 834 | 854 | 875 | 895 | 915 | 936 | 956 | 976 | 997
| 6 | 890 | 916 | 943 | 969 | 995 | 1022 | 1048 | 1074 | 1101 | 1127 | 1153 | 1180 | 1206 | 1232 | 1259 | 1285 | 1311
| 6.5 | 1148 | 1181 | 1215 | 1248 | 1282 | 1315 | 1349 | 1382 | 1415 | 1449 | 1482 | 1516 | 1549 | 1582 | 1616 | 1649 | 1682
| 7 | 1441 | 1483 | 1524 | 1566 | 1607 | 1649 | 1690 | 1732 | 1773 | 1814 | 1856 | 1897 | 1939 | 1980 | 2021 | 2062 | 2104
| 7.5 | 1747 | 1797 | 1847 | 1897 | 1946 | 1996 | 2046 | 2096 | 2145 | 2195 | 2245 | 2294 | 2344 | 2394 | 2443 | 2493 | 2543
| 8 | 2047 | 2105 | 2163 | 2221 | 2279 | 2337 | 2395 | 2453 | 2511 | 2569 | 2627 | 2684 | 2742 | 2800 | 2858 | 2915 | 2973
| 8.5 | 2331 | 2397 | 2462 | 2528 | 2594 | 2660 | 2725 | 2791 | 2856 | 2922 | 2987 | 3053 | 3118 | 3184 | 3249 | 3314 | 3379
| 9 | 2595 | 2668 | 2741 | 2814 | 2886 | 2959 | 3032 | 3105 | 3177 | 3250 | 3323 | 3395 | 3468 | 3540 | 3613 | 3685 | 3758
| 9.5 | 2844 | 2923 | 3003 | 3083 | 3162 | 3242 | 3321 | 3401 | 3480 | 3559 | 3638 | 3718 | 3797 | 3877 | 3954 | 4030 | 4107
| 10 | 3078 | 3164 | 3250 | 3336 | 3422 | 3508 | 3593 | 3679 | 3764 | 3851 | 3937 | 4020 | 4101 | 4182 | 4246 | 4309 | 4371
| 10.5 | 3303 | 3395 | 3487 | 3579 | 3671 | 3762 | 3854 | 3947 | 4039 | 4124 | 4209 | 4282 | 4348 | 4414 | 4465 | 4514 | 4564
| 11 | 3522 | 3620 | 3718 | 3816 | 3914 | 4013 | 4108 | 4196 | 4283 | 4352 | 4421 | 4480 | 4532 | 4585 | 4622 | 4658 | 4695
| 11.5 | 3740 | 3844 | 3948 | 4052 | 4150 | 4242 | 4326 | 4398 | 4469 | 4524 | 4579 | 4624 | 4663 | 4702 | 4727 | 4751 | 4775
| 12 | 3952 | 4062 | 4169 | 4264 | 4349 | 4424 | 4493 | 4551 | 4607 | 4649 | 4690 | 4722 | 4749 | 4775 | 4787 | 4798 | 4809
| 12.5 | 4155 | 4261 | 4355 | 4433 | 4503 | 4564 | 4618 | 4662 | 4705 | 4733 | 4762 | 4781 | 4794 | 4807 | 4809 | 4810 | 4810
| 13 | 4333 | 4424 | 4503 | 4566 | 4621 | 4668 | 4709 | 4740 | 4769 | 4785 | 4800 | 4807 | 4809 | 4810 | 4810 | 4810 | 4810
| 13.5 | 4479 | 4554 | 4618 | 4667 | 4709 | 4742 | 4769 | 4787 | 4804 | 4807 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810
| 14 | 4594 | 4654 | 4704 | 4740 | 4768 | 4788 | 4802 | 4807 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810
| 14.5 | 4681 | 4728 | 4763 | 4786 | 4801 | 4807 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810
| 15 | 4743 | 4775 | 4798 | 4807 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810
| 15.5 | 4782 | 4801 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810
| 16 | 4803 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810
| 16.5 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810
| 17 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810
| 17.5 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810
| 18 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810
| 18.5 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810
| 19 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810
| 19.5 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810
| 20 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810
| 20.5 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810
| 21 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810
| 21.5 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810
| 22 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810
| 22.5 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810 | 4810
| 23 | 4783 | 4783 | 4783 | 4783 | 4783 | 4783 | 4783 | 4783 | 4783 | 4783 | 4783 | 4783 | 4783 | 4783 | 4783 | 4783 | 4783
| 23.5 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 24 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560
| 24.5 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418
| 25 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269
| 25.5 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121
| 26 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764
| 3.5 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208
| 4 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819
| 4.5 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639
| 5 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875
| 5.5 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458
| 6 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111 | 0.56111
| 6.5 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931 | 0.54931
| 7 | 0.52778 | 0.52778 | 0.52778 | 0.52778 | 0.52778 | 0.52778 | 0.52778 | 0.52778 | 0.52778 | 0.52778 | 0.52778 | 0.52778 | 0.52778 | 0.52778 | 0.52778 | 0.52778 | 0.52778
| 7.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
| 8 | 0.46875 | 0.46875 | 0.46875 | 0.46875 | 0.46875 | 0.46875 | 0.46875 | 0.46875 | 0.46875 | 0.46875 | 0.46875 | 0.46875 | 0.46875 | 0.46875 | 0.46875 | 0.46875 | 0.46875
| 8.5 | 0.43611 | 0.43611 | 0.43611 | 0.43611 | 0.43611 | 0.43611 | 0.43611 | 0.43611 | 0.43611 | 0.43611 | 0.43611 | 0.43611 | 0.43611 | 0.43611 | 0.43611 | 0.43611 | 0.43611
| 9 | 0.40208 | 0.40208 | 0.40208 | 0.40208 | 0.40208 | 0.40208 | 0.40208 | 0.40208 | 0.40208 | 0.40208 | 0.40208 | 0.40208 | 0.40208 | 0.40208 | 0.40139 | 0.40069 | 0.4
| 9.5 | 0.36875 | 0.36875 | 0.36875 | 0.36875 | 0.36875 | 0.36875 | 0.36875 | 0.36875 | 0.36875 | 0.36875 | 0.36806 | 0.36736 | 0.36667 | 0.36597 | 0.36458 | 0.36389 | 0.3625
| 10 | 0.33542 | 0.33542 | 0.33542 | 0.33542 | 0.33542 | 0.33542 | 0.33542 | 0.33542 | 0.33472 | 0.33403 | 0.33333 | 0.33194 | 0.33125 | 0.32986 | 0.32778 | 0.32639 | 0.325
| 10.5 | 0.30486 | 0.30486 | 0.30486 | 0.30486 | 0.30486 | 0.30417 | 0.30417 | 0.30278 | 0.30208 | 0.30069 | 0.3 | 0.29792 | 0.29653 | 0.29514 | 0.29306 | 0.29097 | 0.28958
| 11 | 0.27847 | 0.27847 | 0.27847 | 0.27778 | 0.27708 | 0.27639 | 0.275 | 0.27431 | 0.27292 | 0.27153 | 0.26944 | 0.26806 | 0.26597 | 0.26458 | 0.2625 | 0.26042 | 0.25833
| 11.5 | 0.25486 | 0.25486 | 0.25417 | 0.25347 | 0.25208 | 0.25069 | 0.24931 | 0.24792 | 0.24653 | 0.24444 | 0.24306 | 0.24097 | 0.23889 | 0.2375 | 0.23472 | 0.23264 | 0.23056
| 12 | 0.23333 | 0.23264 | 0.23194 | 0.23056 | 0.22917 | 0.22778 | 0.22639 | 0.225 | 0.22292 | 0.22083 | 0.21944 | 0.21736 | 0.21528 | 0.21319 | 0.21042 | 0.20833 | 0.20625
| 12.5 | 0.21458 | 0.21319 | 0.21181 | 0.21042 | 0.20903 | 0.20764 | 0.20556 | 0.20347 | 0.20208 | 0.2 | 0.19792 | 0.19583 | 0.19375 | 0.19167 | 0.18889 | 0.18681 | 0.18403
| 13 | 0.19653 | 0.19514 | 0.19375 | 0.19236 | 0.19097 | 0.18889 | 0.18681 | 0.18472 | 0.18333 | 0.18125 | 0.17917 | 0.17639 | 0.17431 | 0.17222 | 0.16944 | 0.16736 | 0.16458
| 13.5 | 0.18056 | 0.17917 | 0.17778 | 0.17569 | 0.17431 | 0.17222 | 0.17014 | 0.16806 | 0.16597 | 0.16389 | 0.16181 | 0.15972 | 0.15694 | 0.15486 | 0.15208 | 0.15 | 0.14792
| 14 | 0.16597 | 0.16458 | 0.16319 | 0.16111 | 0.15903 | 0.15694 | 0.15486 | 0.15278 | 0.15069 | 0.14861 | 0.14653 | 0.14375 | 0.14167 | 0.13958 | 0.13681 | 0.13472 | 0.13194
| 14.5 | 0.15278 | 0.15139 | 0.14931 | 0.14722 | 0.14514 | 0.14306 | 0.14097 | 0.13889 | 0.13681 | 0.13472 | 0.13264 | 0.12986 | 0.12778 | 0.12569 | 0.12292 | 0.12014 | 0.11806
| 15 | 0.14097 | 0.13889 | 0.1375 | 0.13542 | 0.13333 | 0.13125 | 0.12917 | 0.12639 | 0.12431 | 0.12222 | 0.12014 | 0.11736 | 0.11528 | 0.11319 | 0.11042 | 0.10833 | 0.10625
| 15.5 | 0.12986 | 0.12778 | 0.12639 | 0.12431 | 0.12222 | 0.11944 | 0.11736 | 0.11528 | 0.11319 | 0.11111 | 0.10833 | 0.10625 | 0.10417 | 0.10208 | 0.1 | 0.097917 | 0.096528
| 16 | 0.12014 | 0.11806 | 0.11597 | 0.11389 | 0.11181 | 0.10972 | 0.10764 | 0.10486 | 0.10278 | 0.10069 | 0.098611 | 0.096528 | 0.094444 | 0.092361 | 0.090972 | 0.088889 | 0.0875
| 16.5 | 0.11111 | 0.10903 | 0.10694 | 0.10486 | 0.10278 | 0.10069 | 0.098611 | 0.095833 | 0.09375 | 0.091667 | 0.090278 | 0.088194 | 0.086111 | 0.084722 | 0.083333 | 0.08125 | 0.079861
| 17 | 0.10278 | 0.10139 | 0.099306 | 0.096528 | 0.094444 | 0.092361 | 0.090278 | 0.088194 | 0.086111 | 0.084722 | 0.082639 | 0.08125 | 0.079167 | 0.077778 | 0.076389 | 0.075 | 0.073611
| 17.5 | 0.095833 | 0.09375 | 0.091667 | 0.089583 | 0.0875 | 0.085417 | 0.083333 | 0.081944 | 0.079861 | 0.078472 | 0.076389 | 0.075 | 0.073611 | 0.072222 | 0.070833 | 0.069444 | 0.098
| 18 | 0.089583 | 0.0875 | 0.085417 | 0.083333 | 0.08125 | 0.079861 | 0.077778 | 0.075694 | 0.074306 | 0.072917 | 0.071528 | 0.070139 | 0.099 | 0.097 | 0.095 | 0.093 | 0.092
| 18.5 | 0.084028 | 0.081944 | 0.079861 | 0.078472 | 0.076389 | 0.074306 | 0.072917 | 0.071528 | 0.069444 | 0.098 | 0.096 | 0.094 | 0.093 | 0.091 | 0.089 | 0.088 | 0.086
| 19 | 0.079861 | 0.077778 | 0.075694 | 0.073611 | 0.072222 | 0.070139 | 0.099 | 0.097 | 0.095 | 0.093 | 0.091 | 0.089 | 0.087 | 0.086 | 0.084 | 0.083 | 0.081
| 19.5 | 0.075694 | 0.073611 | 0.071528 | 0.070139 | 0.098 | 0.096 | 0.094 | 0.092 | 0.09 | 0.088 | 0.086 | 0.085 | 0.083 | 0.081 | 0.08 | 0.079 | 0.077
| 20 | 0.071528 | 0.070139 | 0.098 | 0.096 | 0.094 | 0.091 | 0.089 | 0.088 | 0.086 | 0.084 | 0.082 | 0.081 | 0.079 | 0.078 | 0.076 | 0.075 | 0.074
| 20.5 | 0.095 | 0.093 | 0.09 | 0.088 | 0.086 | 0.084 | 0.082 | 0.081 | 0.079 | 0.077 | 0.075 | 0.075 | 0.073 | 0.072 | 0.07 | 0.069 | 0.068
| 21 | 0.087 | 0.085 | 0.082 | 0.081 | 0.079 | 0.077 | 0.075 | 0.074 | 0.072 | 0.071 | 0.069 | 0.068 | 0.066 | 0.066 | 0.064 | 0.063 | 0.062
| 21.5 | 0.078 | 0.077 | 0.075 | 0.073 | 0.072 | 0.069 | 0.068 | 0.067 | 0.066 | 0.064 | 0.062 | 0.062 | 0.06 | 0.059 | 0.058 | 0.057 | 0.056
| 22 | 0.072 | 0.07 | 0.068 | 0.067 | 0.066 | 0.063 | 0.062 | 0.061 | 0.06 | 0.059 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053 | 0.052 | 0.052
| 22.5 | 0.066 | 0.064 | 0.063 | 0.061 | 0.06 | 0.058 | 0.057 | 0.056 | 0.055 | 0.054 | 0.052 | 0.052 | 0.05 | 0.05 | 0.048 | 0.048 | 0.047
| 23 | 0.06 | 0.059 | 0.057 | 0.056 | 0.055 | 0.053 | 0.052 | 0.052 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.046 | 0.045 | 0.044 | 0.043
| 23.5 | 0.055 | 0.054 | 0.052 | 0.051 | 0.05 | 0.048 | 0.047 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.04 | 0.039
| 24 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.04 | 0.039 | 0.038 | 0.037 | 0.037 | 0.036
| 24.5 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.04 | 0.039 | 0.038 | 0.037 | 0.036 | 0.036 | 0.035 | 0.034 | 0.034 | 0.033
| 25 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.038 | 0.037 | 0.037 | 0.036 | 0.035 | 0.034 | 0.034 | 0.033 | 0.033 | 0.032 | 0.031 | 0.031
| 25.5 | 0.04 | 0.039 | 0.038 | 0.037 | 0.036 | 0.035 | 0.034 | 0.034 | 0.033 | 0.032 | 0.032 | 0.031 | 0.03 | 0.03 | 0.029 | 0.029 | 0.028
| 26 | 0.037 | 0.036 | 0.035 | 0.034 | 0.034 | 0.033 | 0.032 | 0.032 | 0.031 | 0.03 | 0.029 | 0.029 | 0.028 | 0.028 | 0.027 | 0.027 | 0.026