## Sheet1
PROPERTIES
General
Name | Nordex N63/5.X Class B 4,7MW
Manufacturer | Nordex
Hub Height | 118 | 120 | 164
Power
Rated Power | 4700
Peak Power | 4700
Power Regulation Type | Pitch
Voltage | 750
Rotor
Rotor diameter | 163
Number of blades | 3
Rated RPM | 11.8
Rotor tilt | 5
Speed Regulation Type | Variable
Wind Speed Control Strategies
Cut-in Wind Speed | 3
Cut-out Wind Speed | 26
Restart Wind Speed | 25.5
Stop Wind Speed | 3
Temperature Control Strategies
Low Temperature Shutdown | -20
Low Temperature Restart | -18
High Temperature Shutdown | 45
High Temperature Restart | 40
Comments and details

## Sheet2
TURBINE CLASIFICATION
Class and Subclass
Turbine Class | S
Turbine SubClass | B
Values
Certification | IEC 3rd Edition
Vave | 6.5-8
Vref | 38.8-40.3
Design TI | 0.16

## Sheet3
POWER CURVE
Power (kW)
Air Density (kg/m³)
TI (%) | 10 | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 18 | 21 | 23 | 25 | 28 | 30 | 32 | 34 | 37 | 39 | 41 | 44 | 46 | 48 | 50 | 53 | 55
| 3.5 | 97 | 101 | 106 | 110 | 115 | 119 | 124 | 128 | 133 | 137 | 142 | 146 | 151 | 155 | 159 | 164 | 168
| 4 | 202 | 209 | 217 | 224 | 231 | 239 | 246 | 254 | 261 | 268 | 276 | 283 | 290 | 298 | 305 | 312 | 320
| 4.5 | 332 | 343 | 354 | 365 | 376 | 387 | 398 | 409 | 420 | 431 | 441 | 452 | 463 | 474 | 485 | 496 | 507
| 5 | 487 | 502 | 517 | 533 | 548 | 563 | 578 | 594 | 609 | 624 | 639 | 655 | 670 | 685 | 700 | 716 | 731
| 5.5 | 671 | 692 | 712 | 732 | 753 | 773 | 793 | 814 | 834 | 854 | 875 | 895 | 915 | 936 | 956 | 976 | 997
| 6 | 890 | 916 | 943 | 969 | 995 | 1022 | 1048 | 1075 | 1101 | 1127 | 1154 | 1180 | 1206 | 1232 | 1259 | 1285 | 1311
| 6.5 | 1147 | 1181 | 1214 | 1248 | 1281 | 1314 | 1348 | 1381 | 1415 | 1448 | 1481 | 1515 | 1548 | 1581 | 1615 | 1648 | 1681
| 7 | 1434 | 1475 | 1516 | 1557 | 1599 | 1640 | 1681 | 1722 | 1764 | 1805 | 1846 | 1887 | 1928 | 1969 | 2011 | 2052 | 2093
| 7.5 | 1725 | 1774 | 1823 | 1873 | 1922 | 1971 | 2020 | 2069 | 2119 | 2168 | 2217 | 2266 | 2315 | 2364 | 2413 | 2462 | 2511
| 8 | 2006 | 2063 | 2120 | 2177 | 2234 | 2291 | 2348 | 2405 | 2461 | 2518 | 2575 | 2631 | 2688 | 2745 | 2801 | 2858 | 2915
| 8.5 | 2269 | 2334 | 2398 | 2462 | 2526 | 2590 | 2654 | 2718 | 2782 | 2846 | 2909 | 2973 | 3037 | 3101 | 3164 | 3228 | 3292
| 9 | 2515 | 2585 | 2656 | 2727 | 2797 | 2868 | 2939 | 3009 | 3080 | 3150 | 3221 | 3291 | 3361 | 3432 | 3502 | 3572 | 3643
| 9.5 | 2745 | 2822 | 2899 | 2976 | 3053 | 3130 | 3207 | 3284 | 3360 | 3437 | 3513 | 3590 | 3667 | 3744 | 3821 | 3895 | 3968
| 10 | 2964 | 3047 | 3130 | 3213 | 3295 | 3378 | 3461 | 3543 | 3626 | 3708 | 3791 | 3875 | 3954 | 4032 | 4110 | 4171 | 4231
| 10.5 | 3175 | 3264 | 3353 | 3441 | 3530 | 3618 | 3706 | 3795 | 3884 | 3971 | 4053 | 4135 | 4203 | 4266 | 4330 | 4377 | 4425
| 11 | 3384 | 3478 | 3572 | 3667 | 3760 | 3855 | 3950 | 4038 | 4123 | 4203 | 4269 | 4336 | 4390 | 4440 | 4491 | 4526 | 4561
| 11.5 | 3590 | 3690 | 3789 | 3889 | 3989 | 4081 | 4169 | 4245 | 4314 | 4378 | 4432 | 4485 | 4526 | 4563 | 4601 | 4624 | 4647
| 12 | 3788 | 3893 | 3998 | 4101 | 4191 | 4269 | 4341 | 4403 | 4459 | 4509 | 4549 | 4589 | 4618 | 4643 | 4668 | 4679 | 4689
| 12.5 | 3978 | 4087 | 4187 | 4277 | 4352 | 4416 | 4474 | 4522 | 4565 | 4602 | 4630 | 4657 | 4673 | 4686 | 4699 | 4699 | 4700
| 13 | 4161 | 4257 | 4342 | 4417 | 4479 | 4528 | 4573 | 4608 | 4638 | 4663 | 4678 | 4693 | 4698 | 4699 | 4700 | 4700 | 4700
| 13.5 | 4313 | 4395 | 4465 | 4526 | 4574 | 4610 | 4642 | 4665 | 4682 | 4695 | 4698 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 14 | 4435 | 4502 | 4559 | 4606 | 4640 | 4664 | 4684 | 4694 | 4698 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 14.5 | 4530 | 4583 | 4626 | 4660 | 4682 | 4693 | 4699 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 15 | 4599 | 4639 | 4669 | 4690 | 4698 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 15.5 | 4648 | 4675 | 4692 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 16 | 4681 | 4694 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 16.5 | 4698 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 17 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 17.5 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 18 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 18.5 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 19 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 19.5 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 20 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 20.5 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 21 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 21.5 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 22 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 22.5 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 23 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700 | 4700
| 23.5 | 4661 | 4661 | 4661 | 4661 | 4661 | 4661 | 4661 | 4661 | 4661 | 4661 | 4661 | 4661 | 4661 | 4661 | 4661 | 4661 | 4661
| 24 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560
| 24.5 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418 | 4418
| 25 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269 | 4269
| 25.5 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121 | 4121
| 26 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973 | 3973

## Sheet4
THRUST CURVE
Ct (-)
Air Density (kg/m³)
|  | 0.9 | 0.925 | 0.95 | 0.975 | 1 | 1.025 | 1.05 | 1.075 | 1.1 | 1.125 | 1.15 | 1.175 | 1.2 | 1.225 | 1.25 | 1.275 | 1.3
Wind Speed (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764 | 0.60764
| 3.5 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208 | 0.60208
| 4 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819
| 4.5 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639 | 0.57639
| 5 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875 | 0.56875
| 5.5 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458 | 0.56458
| 6 | 0.55903 | 0.55903 | 0.55903 | 0.55903 | 0.55903 | 0.55903 | 0.55903 | 0.55903 | 0.55903 | 0.55903 | 0.55903 | 0.55903 | 0.55903 | 0.55903 | 0.55903 | 0.55903 | 0.55903
| 6.5 | 0.54306 | 0.54306 | 0.54306 | 0.54306 | 0.54306 | 0.54306 | 0.54306 | 0.54306 | 0.54306 | 0.54306 | 0.54306 | 0.54306 | 0.54306 | 0.54306 | 0.54306 | 0.54306 | 0.54306
| 7 | 0.51806 | 0.51806 | 0.51806 | 0.51806 | 0.51806 | 0.51806 | 0.51806 | 0.51806 | 0.51806 | 0.51806 | 0.51806 | 0.51806 | 0.51806 | 0.51806 | 0.51806 | 0.51806 | 0.51806
| 7.5 | 0.48819 | 0.48819 | 0.48819 | 0.48819 | 0.48819 | 0.48819 | 0.48819 | 0.48819 | 0.48819 | 0.48819 | 0.48819 | 0.48819 | 0.48819 | 0.48819 | 0.48819 | 0.48819 | 0.48819
| 8 | 0.45556 | 0.45556 | 0.45556 | 0.45556 | 0.45556 | 0.45556 | 0.45556 | 0.45556 | 0.45556 | 0.45556 | 0.45556 | 0.45556 | 0.45556 | 0.45556 | 0.45556 | 0.45556 | 0.45556
| 8.5 | 0.42153 | 0.42153 | 0.42153 | 0.42153 | 0.42153 | 0.42153 | 0.42153 | 0.42153 | 0.42153 | 0.42153 | 0.42153 | 0.42153 | 0.42153 | 0.42153 | 0.42153 | 0.42153 | 0.42153
| 9 | 0.38681 | 0.38681 | 0.38681 | 0.38681 | 0.38681 | 0.38681 | 0.38681 | 0.38681 | 0.38681 | 0.38681 | 0.38681 | 0.38681 | 0.38681 | 0.38681 | 0.38681 | 0.38611 | 0.38542
| 9.5 | 0.35278 | 0.35278 | 0.35278 | 0.35278 | 0.35278 | 0.35278 | 0.35278 | 0.35278 | 0.35278 | 0.35278 | 0.35208 | 0.35208 | 0.35139 | 0.35069 | 0.35 | 0.34931 | 0.34792
| 10 | 0.32014 | 0.32014 | 0.32014 | 0.32014 | 0.32014 | 0.32014 | 0.32014 | 0.32014 | 0.31944 | 0.31944 | 0.31806 | 0.31736 | 0.31667 | 0.31528 | 0.31458 | 0.3125 | 0.31111
| 10.5 | 0.29097 | 0.29097 | 0.29097 | 0.29097 | 0.29097 | 0.29097 | 0.29028 | 0.28958 | 0.28889 | 0.28819 | 0.28681 | 0.28542 | 0.28403 | 0.28264 | 0.28125 | 0.27986 | 0.27778
| 11 | 0.26528 | 0.26528 | 0.26528 | 0.26528 | 0.26458 | 0.26389 | 0.26319 | 0.2625 | 0.26111 | 0.25972 | 0.25833 | 0.25694 | 0.25556 | 0.25347 | 0.25208 | 0.25 | 0.24792
| 11.5 | 0.24306 | 0.24306 | 0.24236 | 0.24236 | 0.24097 | 0.24028 | 0.23889 | 0.2375 | 0.23611 | 0.23472 | 0.23333 | 0.23194 | 0.22986 | 0.22778 | 0.22639 | 0.22431 | 0.22222
| 12 | 0.22292 | 0.22222 | 0.22153 | 0.22083 | 0.22014 | 0.21875 | 0.21736 | 0.21597 | 0.21389 | 0.2125 | 0.21042 | 0.20903 | 0.20694 | 0.20486 | 0.20278 | 0.20069 | 0.19861
| 12.5 | 0.20486 | 0.20417 | 0.20278 | 0.20208 | 0.20069 | 0.19931 | 0.19792 | 0.19583 | 0.19444 | 0.19236 | 0.19028 | 0.18889 | 0.18681 | 0.18472 | 0.18264 | 0.18056 | 0.17778
| 13 | 0.18819 | 0.1875 | 0.18611 | 0.18472 | 0.18333 | 0.18194 | 0.17986 | 0.17847 | 0.17639 | 0.17431 | 0.17222 | 0.17014 | 0.16806 | 0.16597 | 0.16389 | 0.16181 | 0.15972
| 13.5 | 0.17292 | 0.17222 | 0.17083 | 0.16944 | 0.16736 | 0.16597 | 0.16389 | 0.16181 | 0.16042 | 0.15833 | 0.15625 | 0.15417 | 0.15208 | 0.15 | 0.14792 | 0.14514 | 0.14306
| 14 | 0.15972 | 0.15833 | 0.15694 | 0.15486 | 0.15347 | 0.15139 | 0.14931 | 0.14792 | 0.14583 | 0.14375 | 0.14167 | 0.13958 | 0.1375 | 0.13542 | 0.13333 | 0.13056 | 0.12847
| 14.5 | 0.14722 | 0.14514 | 0.14375 | 0.14236 | 0.14028 | 0.13819 | 0.13681 | 0.13472 | 0.13264 | 0.13056 | 0.12847 | 0.12639 | 0.12431 | 0.12153 | 0.11944 | 0.11736 | 0.11528
| 15 | 0.13542 | 0.13403 | 0.13264 | 0.13056 | 0.12847 | 0.12708 | 0.125 | 0.12292 | 0.12083 | 0.11875 | 0.11667 | 0.11458 | 0.1125 | 0.10972 | 0.10764 | 0.10556 | 0.10347
| 15.5 | 0.125 | 0.12361 | 0.12153 | 0.12014 | 0.11806 | 0.11597 | 0.11389 | 0.11181 | 0.10972 | 0.10764 | 0.10556 | 0.10347 | 0.10139 | 0.099306 | 0.097222 | 0.095833 | 0.09375
| 16 | 0.11597 | 0.11389 | 0.1125 | 0.11042 | 0.10833 | 0.10625 | 0.10417 | 0.10208 | 0.1 | 0.097917 | 0.095833 | 0.09375 | 0.092361 | 0.090278 | 0.088889 | 0.086806 | 0.085417
| 16.5 | 0.10694 | 0.10556 | 0.10347 | 0.10208 | 0.1 | 0.097917 | 0.095833 | 0.09375 | 0.091667 | 0.089583 | 0.0875 | 0.086111 | 0.084028 | 0.082639 | 0.08125 | 0.079167 | 0.077778
| 17 | 0.1 | 0.097917 | 0.095833 | 0.094444 | 0.092361 | 0.090278 | 0.088194 | 0.086111 | 0.084028 | 0.082639 | 0.080556 | 0.079167 | 0.077778 | 0.075694 | 0.074306 | 0.072917 | 0.071528
| 17.5 | 0.093056 | 0.090972 | 0.089583 | 0.0875 | 0.085417 | 0.083333 | 0.08125 | 0.079861 | 0.077778 | 0.076389 | 0.075 | 0.072917 | 0.071528 | 0.070139 | 0.099 | 0.098 | 0.096
| 18 | 0.0875 | 0.085417 | 0.083333 | 0.08125 | 0.079861 | 0.077778 | 0.075694 | 0.074306 | 0.072917 | 0.070833 | 0.069444 | 0.098 | 0.096 | 0.094 | 0.093 | 0.091 | 0.089
| 18.5 | 0.081944 | 0.080556 | 0.078472 | 0.076389 | 0.074306 | 0.072917 | 0.070833 | 0.069444 | 0.098 | 0.096 | 0.094 | 0.092 | 0.09 | 0.089 | 0.087 | 0.085 | 0.084
| 19 | 0.077778 | 0.075694 | 0.073611 | 0.072222 | 0.070139 | 0.099 | 0.097 | 0.094 | 0.092 | 0.091 | 0.089 | 0.087 | 0.085 | 0.084 | 0.082 | 0.081 | 0.079
| 19.5 | 0.073611 | 0.071528 | 0.070139 | 0.098 | 0.096 | 0.094 | 0.092 | 0.09 | 0.088 | 0.086 | 0.084 | 0.083 | 0.081 | 0.079 | 0.078 | 0.077 | 0.075
| 20 | 0.070139 | 0.098 | 0.096 | 0.094 | 0.091 | 0.089 | 0.087 | 0.085 | 0.084 | 0.082 | 0.08 | 0.079 | 0.077 | 0.076 | 0.075 | 0.073 | 0.072
| 20.5 | 0.093 | 0.09 | 0.088 | 0.086 | 0.084 | 0.082 | 0.08 | 0.078 | 0.077 | 0.075 | 0.074 | 0.073 | 0.071 | 0.07 | 0.069 | 0.067 | 0.066
| 21 | 0.085 | 0.082 | 0.081 | 0.079 | 0.077 | 0.075 | 0.073 | 0.071 | 0.071 | 0.069 | 0.067 | 0.066 | 0.065 | 0.064 | 0.063 | 0.061 | 0.061
| 21.5 | 0.077 | 0.075 | 0.073 | 0.072 | 0.069 | 0.068 | 0.066 | 0.065 | 0.064 | 0.062 | 0.061 | 0.06 | 0.059 | 0.058 | 0.057 | 0.056 | 0.055
| 22 | 0.07 | 0.068 | 0.067 | 0.066 | 0.063 | 0.062 | 0.061 | 0.059 | 0.059 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053 | 0.052 | 0.051 | 0.05
| 22.5 | 0.064 | 0.063 | 0.061 | 0.06 | 0.058 | 0.057 | 0.056 | 0.054 | 0.054 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.048 | 0.047 | 0.046
| 23 | 0.059 | 0.057 | 0.056 | 0.055 | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.045 | 0.044 | 0.043 | 0.042
| 23.5 | 0.054 | 0.052 | 0.051 | 0.05 | 0.048 | 0.047 | 0.046 | 0.045 | 0.045 | 0.044 | 0.042 | 0.042 | 0.041 | 0.04 | 0.04 | 0.039 | 0.038
| 24 | 0.049 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.038 | 0.037 | 0.037 | 0.036 | 0.035
| 24.5 | 0.045 | 0.044 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.038 | 0.038 | 0.037 | 0.036 | 0.036 | 0.035 | 0.034 | 0.034 | 0.033 | 0.032
| 25 | 0.042 | 0.041 | 0.04 | 0.039 | 0.038 | 0.037 | 0.036 | 0.035 | 0.035 | 0.034 | 0.033 | 0.033 | 0.032 | 0.032 | 0.031 | 0.03 | 0.03
| 25.5 | 0.039 | 0.038 | 0.037 | 0.036 | 0.035 | 0.034 | 0.033 | 0.033 | 0.032 | 0.032 | 0.031 | 0.03 | 0.03 | 0.029 | 0.029 | 0.028 | 0.028
| 26 | 0.036 | 0.035 | 0.034 | 0.034 | 0.033 | 0.032 | 0.031 | 0.03 | 0.03 | 0.029 | 0.029 | 0.028 | 0.028 | 0.027 | 0.027 | 0.026 | 0.026